## Decision Matrix
| Study Segment | [8 empty] | Results |  | Ignition Risk | [12 empty] | Impact
[12 empty] | Environment |  |  |  |  | System
| A | A1 | A2 | B | B1 | B2 | B3 | B4 | C | D | E | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 17 | 18 | Totals | Shutoff
| 96% | [10 empty] | 8% | 12% | 10% | 12% | 10% | 3% | 3% | 2% | 2% | 2% | 2% | 4% | 5% | 12% | 3% | 3% | 3% | 96% | 4%
ndx | Ckt | Op Dist | Sub | Section Start | Section End | Section End | Section End | Section End | Dist (Mi) | Score | Rank | Zone | Wind | Tree | Fuel | Fire Ign. Risk | Cap | Exp Fuse | SWs | Cond | Trans (All) | HR Trans | DOC Rank | Rel Hist | Value Risk | Crit Svc | Bio Rank | Cult Rank |  | Shutoff | DstMlt Score | DstMlt Rank | DstDiv Score | DstDiv Rank
76 | 221 | NE | Santa Ysabel | 221-33R | 221-14 |  |  |  | 28.2432 | 2.5197 | 1 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.71173 | 17 | 8.9225 | 246
168 | 442 | EA | Glencliff | 442-2R | 442-16R | EOC |  |  | 15.3869 | 2.4598 | 2 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 0.37852 | 52 | 15.9876 | 158
98 | 237 | NE | Creelman | P117100 | EOC |  |  |  | 31.21 | 2.3197 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 2 | 3 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.72407 | 16 | 7.4335 | 258
82 | 222 | NE | Santa Ysabel | 222-8 | EOC |  |  |  | 38.3066 | 2.3196 | 4 | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 0.88871 | 6 | 6.0564 | 273
276 | 1030 | NE | Valley Center | 1030-14 | 1030-20R |  |  |  | 40.054 | 2.3196 | 5 | 3 | 2 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 2 | 1 | 1 | 3 |  |  | 0.92925 | 5 | 5.7922 | 276
57 | 212 | NE | Warners | P19585 | EOC |  |  |  | 23.0977 | 2.3098 | 6 | 3 | 3 | 3 | 3 | 3 | 0 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 1 | 0 | 2 | 3 |  |  | 0.53356 | 28 | 10.001 | 235
163 | 440 | EA | Glencliff | 440-6 | EOC |  |  |  | 12.2689 | 2.2899 | 7 | 3 | 2 | 3 | 3 | 3 | 0 | 2 | 2 | 2 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 0.28096 | 88 | 18.665 | 139
206 | 520 | NE | Avocado | 520-33R | 520-1053 |  |  |  | 25.2805 | 2.2897 | 8 | 3 | 3 | 3 | 2 | 3 | 0 | 2 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.57892 | 24 | 9.0584 | 243
251 | 971 | NE | Creelman | 971 | 971-26R |  |  |  | 59.9191 | 2.2894 | 9 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 1.3721 | 1 | 3.8218 | 286
292 | 1233 | NE | Pala | 1233-252R | EOC |  |  |  | 22.833 | 2.2798 | 10 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 0.52059 | 31 | 9.9856 | 237
277 | 1030 | NE | Valley Center | 1030-20R | EOC |  |  |  | 32.6343 | 2.2797 | 11 | 3 | 2 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 1 | 3 | 2 | 2 | 1 | 1 | 3 |  |  | 0.74406 | 13 | 6.9865 | 263
253 | 971 | NE | Creelman | 971-24 | 971-306R | EOC |  |  | 21.5348 | 2.2698 | 12 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.48884 | 33 | 10.5411 | 228
95 | 236 | NE | Creelman | 236 | EOC |  |  |  | 45.9146 | 2.2695 | 13 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 1.0423 | 3 | 4.944 | 282
180 | 448 | EA | Cameron | 448-6 | 448-13R | 448-11R |  |  | 8.9731 | 2.2599 | 14 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.20279 | 132 | 25.1864 | 104
151 | 357 | EA | Alpine | 357 | 357-45R |  |  |  | 11.8898 | 2.2499 | 15 | 3 | 2 | 3 | 2 | 3 | 0 | 3 | 3 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.26752 | 96 | 18.9238 | 137
3 | 73 | EA | Descanso | 73 | 73-49R |  |  |  | 12.8051 | 2.2399 | 16 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 3 | 2 | 2 | 1 | 2 | 2 |  |  | 0.28683 | 82 | 17.493 | 151
155 | 358 | EA | Alpine | 358-14 | EOC |  |  |  | 17.9513 | 2.2398 | 17 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 3 |  |  | 0.40211 | 44 | 12.4782 | 209
74 | 220 | NE | Santa Ysabel | P212213 | EOC |  |  |  | 33.3369 | 2.2297 | 18 | 3 | 3 | 2 | 3 | 3 | 0 | 2 | 1 | 3 | 2 | 2 | 3 | 2 | 2 | 0 | 1 | 2 |  |  | 0.74341 | 14 | 6.6893 | 267
81 | 222 | NE | Santa Ysabel | 222-1370R | EOC |  |  |  | 51 | 2.2295 | 19 | 3 | 3 | 2 | 2 | 3 | 1 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 1.1373 | 2 | 4.3725 | 285
63 | 214 | NE | Rincon | 214-7 | 214-538 | EOC |  |  | 32.9292 | 2.2197 | 20 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 3 | 3 | 1 |  |  | 0.73103 | 15 | 6.7417 | 266
77 | 221 | NE | Santa Ysabel | 221-14 | P519130 | P478409 |  |  | 16.0578 | 2.2098 | 21 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 1 | 3 | 3 | 2 | 1 | 3 | 3 |  |  | 0.35488 | 58 | 13.7628 | 189
219 | 524 | EA | Jamacha | 524-13 | 524-34 |  |  |  | 38.5665 | 2.2096 | 22 | 3 | 1 | 3 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.85232 | 7 | 5.7304 | 277
153 | 357 | EA | Alpine | 357-750R | EOC |  |  |  | 7.1138 | 2.1999 | 23 | 3 | 2 | 3 | 2 | 3 | 0 | 3 | 0 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.1565 | 159 | 30.9257 | 79
152 | 357 | EA | Alpine | 357-45R | 357-750R |  |  |  | 9.7472 | 2.1999 | 24 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.21444 | 126 | 22.5707 | 120
27 | 176 | NE | Poway | 176-26R | EOC |  |  |  | 36.4856 | 2.1996 | 25 | 3 | 1 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 2 |  |  | 0.80268 | 9 | 6.0298 | 274
257 | 972 | NE | Creelman | P13262 | EOC |  |  |  | 15.6979 | 2.1898 | 26 | 3 | 2 | 2 | 3 | 3 | 1 | 2 | 0 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 1 |  |  | 0.34378 | 61 | 13.9509 | 187
4 | 73 | EA | Descanso | 73-49R | 73-23R |  |  |  | 23.0691 | 2.1898 | 27 | 3 | 3 | 1 | 3 | 3 | 1 | 2 | 2 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 |  |  | 0.50521 | 32 | 9.4932 | 241
182 | 448 | EA | Cameron | 448-13R | 448-15R |  |  |  | 12.7725 | 2.1799 | 28 | 3 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 0.27844 | 91 | 17.0679 | 155
103 | 240 | EA | Los Coches | 240 | 240-1097R | 240-1095R |  |  | 13.9318 | 2.1699 | 29 | 3 | 1 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.30232 | 75 | 15.5759 | 165
183 | 448 | EA | Cameron | 448-15R | EOC |  |  |  | 14.9491 | 2.1699 | 30 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.32439 | 67 | 14.516 | 179
179 | 448 | EA | Cameron | 448 | 448-6 |  |  |  | 17.3138 | 2.1698 | 31 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.37571 | 53 | 12.5333 | 205
181 | 448 | EA | Cameron | 448-11R | EOC |  |  |  | 26.1881 | 2.1697 | 32 | 3 | 3 | 1 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.56828 | 26 | 8.2862 | 252
70 | 217 | NE | Rincon | 217 | 217-835R |  |  |  | 45.561 | 2.1695 | 33 | 3 | 3 | 3 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 3 |  |  | 0.98867 | 4 | 4.7628 | 283
162 | 440 | EA | Glencliff | 440 | 440-6 |  |  |  | 8.0581 | 2.1599 | 34 | 3 | 2 | 2 | 3 | 3 | 0 | 1 | 2 | 2 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 0.17406 | 147 | 26.8052 | 96
169 | 442 | EA | Glencliff | 442-16R | EOC |  |  |  | 10.7032 | 2.1599 | 35 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 1 | 1 | 3 | 3 |  |  | 0.23119 | 116 | 20.1808 | 129
154 | 358 | EA | Alpine | 358 | 358-14 |  |  |  | 11.2472 | 2.1599 | 36 | 3 | 2 | 2 | 2 | 3 | 0 | 3 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.24294 | 108 | 19.2048 | 134
202 | 520 | NE | Avocado | 520-35R | 520-11 |  |  |  | 13.8597 | 2.1599 | 37 | 3 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 1 | 2 | 0 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.29937 | 77 | 15.5848 | 163
220 | 524 | EA | Jamacha | 524-34 | EOC |  |  |  | 30.2254 | 2.1497 | 38 | 3 | 1 | 2 | 3 | 3 | 0 | 2 | 0 | 2 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.64985 | 20 | 7.1132 | 262
21 | 157 | EA | Barrett | 157-75R | EOC |  |  |  | 34.9093 | 2.1397 | 39 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.74706 | 12 | 6.1302 | 271
254 | 971 | NE | Creelman | 971-306R | EOC |  |  |  | 17.7968 | 2.1298 | 40 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.37907 | 51 | 11.9685 | 212
101 | 239 | NE | Pala | 239-15R | EOC |  |  |  | 18.8278 | 2.1298 | 41 | 3 | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 3 |  |  | 0.40103 | 46 | 11.313 | 220
201 | 520 | NE | Avocado | 520-26AE | 520-35R |  |  |  | 10.4591 | 2.1199 | 42 | 3 | 2 | 2 | 2 | 3 | 1 | 2 | 1 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 2 |  |  | 0.22173 | 122 | 20.2694 | 128
140 | 351 | NE | Lilac | 351 | 351-819R |  |  |  | 10.6801 | 2.1199 | 43 | 3 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 0.22642 | 120 | 19.85 | 132
144 | 353 | NE | Lilac | 353-914R | EOC |  |  |  | 12.115 | 2.1199 | 44 | 3 | 2 | 3 | 2 | 3 | 1 | 3 | 2 | 1 | 2 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.25684 | 98 | 17.499 | 150
185 | 449 | EA | Cameron | 449-13R | EOC |  |  |  | 13.7621 | 2.1199 | 45 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 1 | 2 |  |  | 0.29176 | 80 | 15.4046 | 167
290 | 1215 | EA | Crestwood | 1215 | EOC |  |  |  | 21.9858 | 2.1198 | 46 | 3 | 3 | 1 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 0 | 2 | 3 | 1 | 1 | 3 | 3 |  |  | 0.4661 | 35 | 9.6426 | 240
73 | 220 | NE | Santa Ysabel | 220-294R | P212213 |  |  |  | 11.5263 | 2.1099 | 47 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 2 | 2 | 0 | 3 | 3 |  |  | 0.24321 | 107 | 18.3059 | 143
294 | 1250 | NE | Olivenhain | 1250 | 1250-9 |  |  |  | 15.9405 | 2.1098 | 48 | 1 | 2 | 3 | 3 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 0.33635 | 62 | 13.2367 | 197
5 | 73 | EA | Descanso | 73-23R | EOC |  |  |  | 18.0922 | 2.1098 | 49 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 |  |  | 0.38175 | 50 | 11.6625 | 216
278 | 1039 | NE | Ash | 1039-13AE | EOC |  |  |  | 13.2862 | 2.0999 | 50 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 2 | 3 | 1 | 1 | 1 |  |  | 0.27901 | 90 | 15.8059 | 160
23 | 157 | EA | Barrett | 157-87R | EOC |  |  |  | 33.3 | 2.0997 | 51 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.6993 | 18 | 6.3063 | 269
240 | 907 | NE | Valley Center | 907 | 907-45 |  |  |  | 11.4294 | 2.0899 | 52 | 3 | 2 | 3 | 2 | 2 | 0 | 3 | 2 | 1 | 2 | 2 | 3 | 2 | 2 | 3 | 1 | 2 |  |  | 0.23887 | 110 | 18.2862 | 144
148 | 355 | EA | Alpine | 355 | EOC |  |  |  | 13.5146 | 2.0899 | 53 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 0 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 0.28245 | 85 | 15.4648 | 166
241 | 907 | NE | Valley Center | 907-45 | EOC |  |  |  | 6.8528 | 2.0799 | 54 | 3 | 2 | 2 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 2 |  |  | 0.14254 | 164 | 30.3524 | 82
149 | 356 | EA | Alpine | 356 | 356-19R |  |  |  | 12.1782 | 2.0799 | 55 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 0.25331 | 100 | 17.0797 | 154
80 | 222 | NE | Santa Ysabel | 222 | 222-1370R | 222-8 |  |  | 14.6 | 2.0799 | 56 | 3 | 3 | 2 | 1 | 3 | 0 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 0.30368 | 74 | 14.2466 | 183
203 | 520 | NE | Avocado | 520-11 | 520-1054 | EOC |  |  | 15.9606 | 2.0798 | 57 | 3 | 2 | 3 | 2 | 3 | 0 | 1 | 1 | 1 | 2 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.33198 | 63 | 13.0321 | 201
25 | 175 | NE | Poway | 175-90R | EOC |  |  |  | 20.7559 | 2.0798 | 58 | 3 | 2 | 2 | 2 | 2 | 1 | 3 | 2 | 1 | 3 | 0 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 0.43172 | 43 | 10.0213 | 234
96 | 237 | NE | Creelman | 237 | 237-8 |  |  |  | 29.9326 | 2.0797 | 59 | 3 | 3 | 3 | 1 | 2 | 1 | 3 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.6226 | 22 | 6.949 | 264
167 | 442 | EA | Glencliff | 442 | 442-2R | EOC |  |  | 2.4383 | 2.07 | 60 | 3 | 3 | 1 | 3 | 3 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 3 | 2 |  |  | 0.050472 | 235 | 84.8967 | 19
288 | 1166 | EA | Loveland | 1166-18R | 1166-1 | EOC |  |  | 8.3159 | 2.0699 | 61 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 0.17214 | 148 | 24.892 | 105
97 | 237 | NE | Creelman | 237-8 | P117100 | EOC |  |  | 14.7367 | 2.0699 | 62 | 3 | 3 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 3 | 1 |  |  | 0.30505 | 73 | 14.0465 | 185
20 | 157 | EA | Barrett | 157-77R | EOC |  |  |  | 40.857 | 2.0696 | 63 | 3 | 3 | 2 | 1 | 2 | 0 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 0.84574 | 8 | 5.0665 | 281
291 | 1233 | NE | Pala | 1233 | 1233-252R |  |  |  | 4.9167 | 2.06 | 64 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 2 | 1 |  |  | 0.10128 | 191 | 41.8983 | 61
66 | 214 | NE | Rincon | 214-16 | EOC |  |  |  | 6.7678 | 2.0599 | 65 | 3 | 3 | 2 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 3 | 2 | 3 |  |  | 0.13942 | 167 | 30.4382 | 81
243 | 908 | NE | Valley Center | 908-23 | EOC |  |  |  | 30.1309 | 2.0597 | 66 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.6207 | 23 | 6.8368 | 265
146 | 354 | NE | Lilac | 354-5 | 354-24AE | EOC |  |  | 36.9813 | 2.0596 | 67 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 3 | 1 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 0.76181 | 11 | 5.5704 | 278
262 | 974 | NE | Creelman | 974-7 | EOC |  |  |  | 15.2072 | 2.0498 | 68 | 3 | 2 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 3 | 3 |  |  | 0.31175 | 70 | 13.4805 | 194
305 | OK1 | NE | Oaks 1 | OK1 | EOC |  |  |  | 8.3875 | 2.0399 | 69 | 3 | 3 | 2 | 3 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | 0.1711 | 149 | 24.3219 | 111
289 | 1166 | EA | Loveland | 1166-1 | EOC |  |  |  | 10.6926 | 2.0399 | 70 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 2 |  |  | 0.21813 | 123 | 19.0786 | 135
160 | 411 | EA | Granite | 411-14R | 411-8 |  |  |  | 17.7886 | 2.0398 | 71 | 1 | 1 | 3 | 2 | 3 | 3 | 3 | 2 | 2 | 3 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.36289 | 54 | 11.468 | 218
55 | 211 | NE | Warners | 211-262R | EOC |  |  |  | 17.1311 | 2.0298 | 72 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 1 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 0.34776 | 59 | 11.8498 | 214
232 | 599 | NE | San Marcos | P116474 | 599-1181 | EOC |  |  | 17.6703 | 2.0298 | 73 | 1 | 1 | 3 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 2 | 2 | 3 | 1 | 1 | 2 |  |  | 0.35871 | 56 | 11.4882 | 217
186 | 449 | EA | Cameron | 449-1 | EOC |  |  |  | 5.9386 | 2.0199 | 74 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 0 | 3 | 3 |  |  | 0.11996 | 181 | 34.0145 | 72
297 | CTL1 | NE | Crestline | CTL1 | EOC |  |  |  | 4.1521 | 2 | 75 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 0 | 2 | 0 | 1 | 2 |  |  | 0.083042 | 202 | 48.1686 | 41
306 | PE1 | NE | Pine Hills | PE1 | EOC |  |  |  | 6.8367 | 1.9999 | 76 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | 0.13673 | 170 | 29.2537 | 89
142 | 352 | NE | Lilac | 352 | EOC |  |  |  | 11.4432 | 1.9999 | 77 | 3 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 0 | 1 | 2 |  |  | 0.22886 | 118 | 17.4777 | 153
258 | 972 | NE | Creelman | 972-4 | EOC |  |  |  | 14.9597 | 1.9999 | 78 | 3 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.29919 | 78 | 13.3693 | 196
295 | 1458 | EA | Alpine | 1458 | 1458-22 | EOC |  |  | 8.5532 | 1.9899 | 79 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 3 |  |  | 0.17021 | 150 | 23.2661 | 117
64 | 214 | NE | Rincon | 214-538 | 214-15 | 214-16 |  |  | 9.3754 | 1.9899 | 80 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 3 | 3 | 1 | 3 | 1 | 2 |  |  | 0.18657 | 138 | 21.2258 | 122
184 | 449 | EA | Cameron | 449 | 449-1 | 449-13R |  |  | 11.3814 | 1.9899 | 81 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 1 | 2 |  |  | 0.22649 | 119 | 17.4846 | 152
75 | 221 | NE | Santa Ysabel | 221 | 221-33R |  |  |  | 4.5674 | 1.98 | 82 | 3 | 3 | 1 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.090435 | 198 | 43.3505 | 56
314 | SL1 | NE | Salton | SL1 | EOC |  |  |  | 4.8994 | 1.98 | 83 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | 0.097009 | 193 | 40.4128 | 63
164 | 441 | EA | Glencliff | 441 | 441-27R | 441-30R |  |  | 10.8778 | 1.9799 | 84 | 3 | 2 | 1 | 3 | 3 | 1 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.21538 | 125 | 18.2021 | 145
14 | 79 | EA | Descanso | 79-676R | 79-658R | EOC |  |  | 15.6057 | 1.9798 | 85 | 3 | 3 | 2 | 2 | 2 | 0 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 0.30899 | 72 | 12.6877 | 203
100 | 239 | NE | Pala | 239 | 239-15R | EOC | EOC |  | 22.1875 | 1.9798 | 86 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 1 |  |  | 0.43931 | 38 | 8.9239 | 245
71 | 217 | NE | Rincon | 217-835R | EOC |  |  |  | 26.3307 | 1.9797 | 87 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.52135 | 30 | 7.5197 | 257
105 | 240 | EA | Los Coches | 240-1095R | EOC |  |  |  | 9.6335 | 1.9699 | 88 | 3 | 1 | 2 | 3 | 3 | 0 | 1 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 2 | 2 |  |  | 0.18978 | 137 | 20.4494 | 127
273 | 1021 | NE | Lilac | 1021-48 | EOC |  |  |  | 12.9259 | 1.9699 | 89 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 1 | 2 |  |  | 0.25464 | 99 | 15.2407 | 168
193 | 470 | NE | Felicita | 470-18R | EOC |  |  |  | 23.211 | 1.9698 | 90 | 1 | 1 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 0 | 3 | 3 | 3 | 1 | 3 | 3 |  |  | 0.45726 | 36 | 8.4874 | 251
296 | 1458 | EA | Alpine | 1458-22 | EOC |  |  |  | 9.3439 | 1.9599 | 91 | 3 | 2 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.18314 | 140 | 20.9762 | 125
141 | 351 | NE | Lilac | 351-819R | EOC |  |  |  | 10.5955 | 1.9599 | 92 | 1 | 2 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 2 | 1 |  |  | 0.20767 | 131 | 18.4985 | 140
68 | 215 | NE | Rincon | P216869 | EOC |  |  |  | 15.0229 | 1.9598 | 93 | 3 | 3 | 2 | 2 | 2 | 0 | 2 | 0 | 1 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.29445 | 79 | 13.0467 | 200
138 | 350 | NE | Lilac | 350-46R | EOC |  |  |  | 20.2322 | 1.9598 | 94 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 0.39655 | 48 | 9.6875 | 239
54 | 211 | NE | Warners | 211-280R | EOC |  |  |  | 13.5968 | 1.9499 | 95 | 1 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 2 | 1 | 1 | 3 | 3 | 1 | 1 | 1 | 3 |  |  | 0.26514 | 97 | 14.3416 | 181
285 | 1138 | EA | Santee | 1138-6R | EOC |  |  |  | 13.9085 | 1.9499 | 96 | 3 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.27122 | 95 | 14.0202 | 186
256 | 972 | NE | Creelman | 972-7 | P13262 |  |  |  | 15.3739 | 1.9498 | 97 | 3 | 2 | 3 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.29979 | 76 | 12.6839 | 204
136 | 350 | NE | Lilac | 350-684R | EOC |  |  |  | 33.1557 | 1.9497 | 98 | 1 | 2 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.64654 | 21 | 5.8813 | 275
316 | TM1 | NE | Temecula (SCE) | TM1 | EOC |  |  |  | 2.9864 | 1.94 | 99 | 3 | 2 | 1 | 3 | 3 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 0 | 1 | 2 |  |  | 0.057935 | 228 | 64.9619 | 27
252 | 971 | NE | Creelman | 971-26R | 971-24 |  |  |  | 9.2403 | 1.9399 | 100 | 3 | 2 | 2 | 3 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.17926 | 143 | 20.9949 | 124
150 | 356 | EA | Alpine | 356-19R | EOC |  |  |  | 14.9436 | 1.9399 | 101 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 3 | 1 | 1 | 2 |  |  | 0.28991 | 81 | 12.9822 | 202
242 | 908 | NE | Valley Center | 908 | 908-23 |  |  |  | 41.2864 | 1.9396 | 102 | 3 | 2 | 3 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.80096 | 10 | 4.6989 | 284
52 | 210 | NE | Warners | P227546 | EOC |  |  |  | 10.2898 | 1.9299 | 103 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 2 | 2 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.19859 | 134 | 18.7565 | 138
24 | 175 | NE | Poway | 175-24R | 175-90R |  |  |  | 14.2606 | 1.9299 | 104 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 3 | 3 |  |  | 0.27523 | 93 | 13.5338 | 193
178 | 445 | EA | Boulevard | 445-24R | EOC |  |  |  | 22.6352 | 1.9298 | 105 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 0 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.43686 | 40 | 8.5265 | 250
56 | 212 | NE | Warners | 212 | P19585 | 212-632R | 212-630R |  | 23.6792 | 1.9298 | 106 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 3 | 3 | 2 | 0 | 3 | 3 | 1 | 0 | 2 | 2 |  |  | 0.45701 | 37 | 8.1506 | 253
72 | 220 | NE | Santa Ysabel | 220 | 220-294R |  |  |  | 7.4 | 1.9199 | 107 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 2 | 2 | 0 | 2 | 1 |  |  | 0.14208 | 166 | 25.9459 | 101
10 | 78 | EA | Descanso | 78 | EOC |  |  |  | 12.1587 | 1.9099 | 108 | 3 | 3 | 1 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 3 | 3 |  |  | 0.23223 | 114 | 15.7089 | 162
173 | 445 | EA | Boulevard | 445 | 445-23R | 445-17R | 445-19R | 445-21R | 11.1438 | 1.8999 | 109 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 3 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.21173 | 128 | 17.0499 | 156
135 | 350 | NE | Lilac | 350 | 350-15R | 350-684R | 350-33R |  | 14.4254 | 1.8999 | 110 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.27408 | 94 | 13.1712 | 199
272 | 1021 | NE | Lilac | 1021 | 1021-48 |  |  |  | 16.2631 | 1.8998 | 111 | 3 | 1 | 2 | 3 | 2 | 0 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 1 | 1 |  |  | 0.309 | 71 | 11.6829 | 215
200 | 520 | NE | Avocado | 520 | 520-18R | 520-26AE |  |  | 18.6953 | 1.8998 | 112 | 1 | 2 | 2 | 2 | 3 | 0 | 3 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.35521 | 57 | 10.163 | 233
51 | 210 | NE | Warners | 210-9R | P227546 | EOC |  |  | 4.0625 | 1.89 | 113 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 3 |  |  | 0.076781 | 208 | 46.5231 | 50
205 | 520 | NE | Avocado | 520-18R | 520-33R |  |  |  | 7.3201 | 1.8899 | 114 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.13835 | 168 | 25.8194 | 103
207 | 520 | NE | Avocado | 520-1053 | EOC |  |  |  | 17.4259 | 1.8898 | 115 | 1 | 2 | 2 | 2 | 3 | 0 | 1 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 2 |  |  | 0.32935 | 64 | 10.8459 | 226
174 | 445 | EA | Boulevard | 445-17R | EOC |  |  |  | 21.1485 | 1.8898 | 116 | 3 | 3 | 1 | 2 | 3 | 0 | 2 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.39971 | 47 | 8.9368 | 244
61 | 212 | NE | Warners | 212-652R | EOC |  |  |  | 28.8727 | 1.8897 | 117 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 0 | 2 | 2 | 2 | 3 | 3 | 1 | 0 | 2 | 2 |  |  | 0.54569 | 27 | 6.546 | 268
177 | 445 | EA | Boulevard | 445-23R | 445-24R | EOC |  |  | 1.2598 | 1.88 | 118 | 3 | 3 | 1 | 2 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.023685 | 260 | 149.2243 | 9
261 | 974 | NE | Creelman | 974 | 974-7 |  |  |  | 6.3195 | 1.8799 | 119 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 3 | 3 |  |  | 0.11881 | 182 | 29.7492 | 86
175 | 445 | EA | Boulevard | 445-19R | EOC |  |  |  | 12.8462 | 1.8799 | 120 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.24151 | 109 | 14.6347 | 178
139 | 350 | NE | Lilac | 350-33R | EOC |  |  |  | 15.0167 | 1.8798 | 121 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.28231 | 86 | 12.5194 | 206
114 | 249 | NE | Pala | 249 | EOC |  |  |  | 15.0523 | 1.8798 | 122 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 0 | 3 | 2 | 2 | 0 | 3 | 3 |  |  | 0.28298 | 84 | 12.4898 | 207
287 | 1166 | EA | Loveland | 1166 | 1166-18R | EOC |  |  | 4.3964 | 1.87 | 123 | 3 | 2 | 1 | 3 | 3 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 2 | 1 |  |  | 0.082213 | 203 | 42.5348 | 59
15 | 79 | EA | Descanso | 79-658R | 79-660R |  |  |  | 13.2152 | 1.8699 | 124 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.24712 | 103 | 14.1504 | 184
53 | 211 | NE | Warners | 211 | 211-280R | 211-262R |  |  | 15.0354 | 1.8698 | 125 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 0.28116 | 87 | 12.4373 | 210
303 | MAN1 | NE | Manzanita | MAN1 | EOC |  |  |  | 3.9542 | 1.86 | 126 | 3 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 0.073548 | 212 | 47.039 | 48
274 | 1022 | NE | Lilac | 1022-15 | EOC |  |  |  | 7.8924 | 1.8599 | 127 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 0 | 3 | 2 | 1 | 1 |  |  | 0.1468 | 160 | 23.5669 | 114
259 | 973 | NE | Creelman | 973 | 973-27 | EOC |  |  | 12.5491 | 1.8599 | 128 | 3 | 2 | 1 | 1 | 3 | 1 | 2 | 3 | 0 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 0.23341 | 113 | 14.8218 | 174
176 | 445 | EA | Boulevard | 445-21R | EOC |  |  |  | 25.8837 | 1.8597 | 129 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.48144 | 34 | 7.186 | 260
170 | 444 | EA | Boulevard | 444 | P41993 |  |  |  | 6.5136 | 1.8499 | 130 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 1 | 1 | 1 | 3 |  |  | 0.1205 | 180 | 28.402 | 90
16 | 79 | EA | Descanso | 79-660R | 79-19R |  |  |  | 7.7002 | 1.8499 | 131 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.14245 | 165 | 24.0254 | 112
104 | 240 | EA | Los Coches | 240-1097R | EOC |  |  |  | 12.7585 | 1.8499 | 132 | 3 | 1 | 1 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.23603 | 112 | 14.5001 | 180
60 | 212 | NE | Warners | 212-650R | EOC |  |  |  | 21.3939 | 1.8498 | 133 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 3 | 3 | 3 | 1 | 0 | 2 | 1 |  |  | 0.39579 | 49 | 8.6473 | 248
172 | 444 | EA | Boulevard | P42077 | EOC |  |  |  | 23.6938 | 1.8498 | 134 | 1 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 0 | 2 | 3 | 1 | 1 | 2 | 3 |  |  | 0.43833 | 39 | 7.808 | 255
22 | 157 | EA | Barrett | 157-67R | 157-87R | 157-75R | 157-77R |  | 2.1 | 1.84 | 135 | 3 | 3 | 0 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 3 | 1 |  |  | 0.03864 | 244 | 87.619 | 18
275 | 1030 | NE | Valley Center | 1030 | 1030-14 |  |  |  | 4.7856 | 1.84 | 136 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 3 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.088055 | 199 | 38.4486 | 65
166 | 441 | EA | Glencliff | 441-30R | EOC |  |  |  | 6.1053 | 1.8399 | 137 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.11234 | 185 | 30.1377 | 85
211 | 521 | NE | Avocado | 521-32R | EOC |  |  |  | 9.1759 | 1.8399 | 138 | 3 | 2 | 2 | 1 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 0.16884 | 151 | 20.0524 | 131
58 | 212 | NE | Warners | 212-632R | 212-650R | 212-652R |  |  | 11.8131 | 1.8399 | 139 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 0 | 2 | 2 | 1 | 3 | 3 | 1 | 0 | 1 | 2 |  |  | 0.21736 | 124 | 15.576 | 164
145 | 354 | NE | Lilac | 354 | 354-5 |  |  |  | 17.6538 | 1.8398 | 140 | 1 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.32483 | 66 | 10.4227 | 230
171 | 444 | EA | Boulevard | P41993 | P42077 |  |  |  | 7.8121 | 1.8299 | 141 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 1 | 1 | 1 | 3 |  |  | 0.14296 | 163 | 23.4251 | 115
1 | 67 | EA | Barrett | 67 | 67-24R |  |  |  | 35.8356 | 1.8296 | 142 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 2 |  |  | 0.65579 | 19 | 5.1067 | 280
65 | 214 | NE | Rincon | 214-15 | EOC |  |  |  | 3.8729 | 1.82 | 143 | 3 | 2 | 1 | 2 | 3 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 3 | 3 | 2 |  |  | 0.070487 | 215 | 46.993 | 49
50 | 210 | NE | Warners | 210 | 210-9R |  |  |  | 6.1955 | 1.8199 | 144 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 1 |  |  | 0.11276 | 184 | 29.3764 | 87
165 | 441 | EA | Glencliff | 441-27R | EOC |  |  |  | 6.7186 | 1.8199 | 145 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.12228 | 177 | 27.0891 | 94
231 | 597 | NE | San Marcos | 597-636 | EOC |  |  |  | 12.7426 | 1.8199 | 146 | 1 | 1 | 3 | 2 | 2 | 0 | 3 | 1 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 2 | 2 |  |  | 0.23192 | 115 | 14.2828 | 182
87 | 230 | NE | Monserate | 230-133 | EOC |  |  |  | 17.6042 | 1.8198 | 147 | 3 | 1 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.3204 | 68 | 10.3385 | 231
311 | RB1 | NE | Rainbow 1 | RB1-19R | EOC |  |  |  | 5.9968 | 1.8099 | 148 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 0 | 2 | 2 | 1 | 1 |  |  | 0.10854 | 188 | 30.1829 | 84
69 | 216 | NE | Rincon | 216 | EOC |  |  |  | 6.6792 | 1.8099 | 149 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 0 | 3 | 3 |  |  | 0.12089 | 178 | 27.0992 | 93
59 | 212 | NE | Warners | 212-630R | EOC |  |  |  | 3.6169 | 1.8 | 150 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 3 | 1 | 0 | 3 | 1 |  |  | 0.065103 | 219 | 49.767 | 36
213 | 521 | NE | Avocado | 521-14R | EOC |  |  |  | 11.8812 | 1.7999 | 151 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 2 | 2 | 1 | 2 | 3 | 2 | 1 | 2 | 2 |  |  | 0.21386 | 127 | 15.1499 | 170
91 | 233 | NE | Monserate | 233-49 | EOC |  |  |  | 24.2447 | 1.7998 | 152 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 0.4364 | 41 | 7.4243 | 259
302 | JU1 | NE | Julian | JU1 | EOC |  |  |  | 2.5316 | 1.79 | 153 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 |  |  | 0.045316 | 237 | 70.7055 | 25
204 | 520 | NE | Avocado | 520-1054 | 520-13 |  |  |  | 5.1127 | 1.7899 | 154 | 3 | 2 | 1 | 2 | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.091517 | 196 | 35.0109 | 69
67 | 215 | NE | Rincon | 215 | P216869 |  |  |  | 8.8807 | 1.7899 | 155 | 3 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.15896 | 158 | 20.1561 | 130
92 | 233 | NE | Monserate | 233-14 | EOC |  |  |  | 22.4464 | 1.7898 | 156 | 1 | 1 | 3 | 1 | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 3 |  |  | 0.40179 | 45 | 7.9746 | 254
137 | 350 | NE | Lilac | 350-15R | 350-46R |  |  |  | 29.4682 | 1.7897 | 157 | 1 | 2 | 2 | 2 | 2 | 0 | 3 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.52748 | 29 | 6.0743 | 272
93 | 234 | NE | Monserate | 234 | EOC |  |  |  | 17.8201 | 1.7798 | 158 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.3172 | 69 | 9.9887 | 236
161 | 411 | EA | Granite | 411-8 | EOC |  |  |  | 7.1159 | 1.7699 | 159 | 1 | 1 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.12595 | 176 | 24.8738 | 106
208 | 521 | NE | Avocado | 521 | 521-27R | 521-18R |  |  | 14.1765 | 1.7699 | 160 | 3 | 2 | 3 | 1 | 1 | 0 | 3 | 3 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.25092 | 101 | 12.4854 | 208
84 | 230 | NE | Monserate | 230-4R | 230-11 | EOC |  |  | 24.6432 | 1.7698 | 161 | 3 | 1 | 3 | 1 | 2 | 2 | 3 | 1 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.43618 | 42 | 7.1825 | 261
11 | 79 | EA | Descanso | 79 | 79-676R | 79-673R |  |  | 6.5 | 1.7599 | 162 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.1144 | 183 | 27.0769 | 95
17 | 79 | EA | Descanso | 79-19R | EOC |  |  |  | 9.0712 | 1.7599 | 163 | 3 | 3 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 1 |  |  | 0.15965 | 156 | 19.402 | 133
102 | 239 | NE | Pala | EOC | EOC |  |  |  | 11.9314 | 1.7599 | 164 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 2 | 1 |  |  | 0.20999 | 129 | 14.7509 | 175
8 | 75 | EA | Jamacha | 75-32R | P171361 |  |  |  | 16.2623 | 1.7598 | 165 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 1 | 2 | 2 | 0 | 3 | 3 | 2 | 3 | 1 | 2 |  |  | 0.28622 | 83 | 10.8226 | 227
88 | 231 | NE | Monserate | 231 | Z317920 |  |  |  | 32.7089 | 1.7397 | 166 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.56913 | 25 | 5.3197 | 279
147 | 354 | NE | Lilac | 354-24AE | EOC |  |  |  | 3.5104 | 1.71 | 167 | 1 | 2 | 1 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 0.060028 | 224 | 48.7122 | 40
310 | RB1 | NE | Rainbow 1 | RB1 | RB1-19R |  |  |  | 9.328 | 1.7099 | 168 | 3 | 2 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 1 | 1 |  |  | 0.15951 | 157 | 18.3318 | 142
260 | 973 | NE | Creelman | 973-626R | EOC |  |  |  | 10.7032 | 1.6999 | 169 | 3 | 2 | 1 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 3 | 2 | 2 | 1 | 1 | 1 |  |  | 0.18195 | 141 | 15.8831 | 159
117 | 283 | EA | Loveland | 283 | 283-29 |  |  |  | 5.4028 | 1.6899 | 170 | 3 | 2 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.091308 | 197 | 31.2798 | 78
209 | 521 | NE | Avocado | 521-18R | 521-5 |  |  |  | 11.3989 | 1.6899 | 171 | 3 | 3 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.19264 | 135 | 14.826 | 173
158 | 396 | EA | Santee | P970961 | EOC |  |  |  | 12.3117 | 1.6899 | 172 | 1 | 1 | 3 | 2 | 3 | 0 | 2 | 1 | 2 | 2 | 0 | 1 | 3 | 2 | 0 | 1 | 1 |  |  | 0.20807 | 130 | 13.7267 | 191
13 | 79 | EA | Descanso | Z371551 | P377371 | EOC |  |  | 2.1905 | 1.68 | 173 | 3 | 3 | 0 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.036801 | 247 | 76.6938 | 23
298 | DV1 | EA | Dehesa Valley | DV1 | EOC |  |  |  | 5.9562 | 1.6799 | 174 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 0 | 1 | 2 | 0 | 2 | 0 | 2 | 1 | 2 | 1 |  |  | 0.10007 | 192 | 28.2057 | 92
212 | 521 | NE | Avocado | 521-27R | 521-14R |  |  |  | 19.5106 | 1.6798 | 175 | 1 | 3 | 2 | 1 | 1 | 1 | 3 | 2 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.32778 | 65 | 8.6107 | 249
113 | 248 | EA | Los Coches | 248 | EOC |  |  |  | 21.5934 | 1.6798 | 176 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 0.36277 | 55 | 7.7802 | 256
271 | 1001 | NC | Rancho Santa Fe | 1001-39 | EOC |  |  |  | 4.7752 | 1.67 | 177 | 1 | 1 | 3 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 1 |  |  | 0.079746 | 206 | 34.9724 | 70
19 | 91 | EA | Jamacha | P370004 | EOC |  |  |  | 5.7009 | 1.6699 | 178 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | 1 |  |  | 0.095206 | 194 | 29.2934 | 88
245 | 909 | NE | Valley Center | 909-6 | EOC |  |  |  | 11.1458 | 1.6699 | 179 | 3 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 2 | 2 | 0 | 3 | 3 |  |  | 0.18614 | 139 | 14.9832 | 172
233 | 599 | NE | San Marcos | 599-1181 | EOC |  |  |  | 6.2038 | 1.6599 | 180 | 1 | 1 | 1 | 3 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 2 | 2 | 3 | 1 | 1 | 2 |  |  | 0.10298 | 189 | 26.7578 | 97
143 | 353 | NE | Lilac | 353 | 353-914R |  |  |  | 6.7023 | 1.6599 | 181 | 1 | 2 | 1 | 2 | 3 | 0 | 2 | 2 | 0 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.11126 | 186 | 24.7677 | 107
2 | 67 | EA | Barrett | 67-24R | EOC |  |  |  | 12.1398 | 1.6599 | 182 | 3 | 2 | 2 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.20152 | 133 | 13.6741 | 192
6 | 75 | EA | Jamacha | 75-996R | 75-40 |  |  |  | 14.7434 | 1.6599 | 183 | 1 | 1 | 2 | 1 | 2 | 1 | 3 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 3 | 2 | 2 |  |  | 0.24474 | 104 | 11.2593 | 222
90 | 233 | NE | Monserate | 233 | 233-49 | 233-14 |  |  | 16.7288 | 1.6598 | 184 | 1 | 1 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.2777 | 92 | 9.923 | 238
157 | 387 | EA | Granite | Z272783 | EOC |  |  |  | 3.4345 | 1.65 | 185 | 1 | 2 | 0 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 1 | 2 | 2 |  |  | 0.056669 | 230 | 48.0424 | 42
78 | 221 | NE | Santa Ysabel | P519130 | EOC |  |  |  | 14.7973 | 1.6499 | 186 | 3 | 3 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.24416 | 106 | 11.1506 | 223
125 | 307 | NC | Rancho Santa Fe | EOC | EOC |  |  |  | 3.7222 | 1.64 | 187 | 1 | 2 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 3 | 2 |  |  | 0.061043 | 222 | 44.0604 | 55
247 | 920 | NE | Pomerado | P108024 | EOC |  |  |  | 4.9241 | 1.64 | 188 | 1 | 1 | 1 | 3 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.080754 | 205 | 33.3059 | 74
307 | RA1 | NE | Ramona | RA1 | EOC |  |  |  | 10.767 | 1.6399 | 189 | 3 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.17658 | 144 | 15.2317 | 169
215 | 522 | NE | Avocado | 522-25 | EOC |  |  |  | 14.515 | 1.6399 | 190 | 1 | 2 | 3 | 1 | 1 | 1 | 3 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.23805 | 111 | 11.2987 | 221
12 | 79 | EA | Descanso | 79-673R | Z371551 |  |  |  | 10.3 | 1.6199 | 191 | 3 | 3 | 0 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.16686 | 153 | 15.7282 | 161
26 | 176 | NE | Poway | 176 | 176-26R | 176-36R |  |  | 14.0405 | 1.6099 | 192 | 1 | 1 | 2 | 2 | 2 | 0 | 3 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.22605 | 121 | 11.4668 | 219
244 | 909 | NE | Valley Center | 909 | 909-6 |  |  |  | 17.4189 | 1.6098 | 193 | 3 | 2 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 2 | 0 | 1 | 2 |  |  | 0.28044 | 89 | 9.2428 | 242
9 | 75 | EA | Jamacha | P171361 | EOC |  |  |  | 15.3894 | 1.5898 | 194 | 3 | 1 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 1 | 0 | 3 | 3 | 1 | 3 | 3 | 3 |  |  | 0.24469 | 105 | 10.3318 | 232
246 | 920 | NE | Pomerado | P137565 | EOC |  |  |  | 1.989 | 1.57 | 195 | 1 | 1 | 0 | 3 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 3 | 1 |  |  | 0.031228 | 251 | 78.9335 | 22
304 | MOR1 | NE | Moore | MOR1 | EOC |  |  |  | 2.8384 | 1.57 | 196 | 3 | 2 | 2 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 0.044564 | 238 | 55.3119 | 33
210 | 521 | NE | Avocado | 521-5 | 521-32R |  |  |  | 10.7176 | 1.5699 | 197 | 3 | 2 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 0.16827 | 152 | 14.6488 | 177
110 | 246 | EA | Los Coches | 246-9 | 246-11 |  |  |  | 11.429 | 1.5699 | 198 | 1 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 1 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 3 |  |  | 0.17943 | 142 | 13.737 | 190
218 | 524 | EA | Jamacha | 524-30 | 524-13 |  |  |  | 3.272 | 1.56 | 199 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.051043 | 234 | 47.6777 | 45
194 | 470 | NE | Felicita | 470-30 | EOC |  |  |  | 5.5282 | 1.5599 | 200 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.08624 | 200 | 28.2188 | 91
187 | 450 | NE | Ash | 450-18 | EOC |  |  |  | 8.5977 | 1.5599 | 201 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 3 | 1 | 1 | 1 | 2 |  |  | 0.13412 | 171 | 18.1443 | 147
28 | 176 | NE | Poway | 176-36R | EOC |  |  |  | 8.5275 | 1.5499 | 202 | 3 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.13218 | 172 | 18.1766 | 146
94 | 235 | NE | Creelman | 235 | EOC |  |  |  | 14.8273 | 1.5499 | 203 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 2 | 2 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.22982 | 117 | 10.4537 | 229
159 | 411 | EA | Granite | P172406 | 411-14R |  |  |  | 1.8231 | 1.53 | 204 | 1 | 1 | 0 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 1 | 2 | 2 |  |  | 0.027894 | 256 | 83.9227 | 20
255 | 972 | NE | Creelman | 972 | 972-7 | 972-4 |  |  | 7.2384 | 1.5299 | 205 | 1 | 2 | 2 | 1 | 1 | 1 | 3 | 3 | 1 | 2 | 0 | 1 | 3 | 2 | 2 | 1 | 1 |  |  | 0.11075 | 187 | 21.1371 | 123
230 | 597 | NE | San Marcos | 597-35 | 597-636 |  |  |  | 4.582 | 1.52 | 206 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 3 | 1 | 2 | 1 |  |  | 0.069647 | 216 | 33.1732 | 75
118 | 283 | EA | Loveland | 283-29 | 283-26 |  |  |  | 8.5809 | 1.5199 | 207 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 2 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 1 | 2 |  |  | 0.13043 | 174 | 17.7138 | 149
45 | 204 | OC | San Mateo | 204-6 | EOC |  |  |  | 8.9962 | 1.5199 | 208 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.13674 | 169 | 16.896 | 157
7 | 75 | EA | Jamacha | 75-40 | 75-32R |  |  |  | 10.9716 | 1.5199 | 209 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 2 | 3 | 1 | 1 |  |  | 0.16677 | 154 | 13.854 | 188
44 | 204 | OC | San Mateo | 204-2 | 204-6 |  |  |  | 12.6553 | 1.5199 | 210 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.19236 | 136 | 12.0108 | 211
119 | 283 | EA | Loveland | 283-26 | EOC |  |  |  | 4.7106 | 1.51 | 211 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.07113 | 214 | 32.0553 | 77
315 | SSC1 | OC | So San Clemente | SSC1 | SSC1-3 |  |  |  | 1.1203 | 1.5 | 212 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 |  |  | 0.016804 | 270 | 133.8969 | 11
62 | 214 | NE | Rincon | 214 | 214-10 | 214-7 |  |  | 8.1002 | 1.4899 | 213 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 3 | 1 | 1 |  |  | 0.12069 | 179 | 18.3946 | 141
129 | 327 | NE | Warren Canyon | 327 | EOC |  |  |  | 0.88636 | 1.48 | 214 | 1 | 2 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 | 3 | 1 |  |  | 0.013118 | 273 | 166.9744 | 8
286 | 1138 | EA | Santee | 1138-22 | EOC |  |  |  | 2.4225 | 1.48 | 215 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.035854 | 249 | 61.093 | 30
293 | 1235 | NE | Monserate | 1235 | EOC |  |  |  | 16.8837 | 1.4798 | 216 | 1 | 2 | 3 | 1 | 1 | 0 | 3 | 2 | 2 | 3 | 0 | 2 | 0 | 2 | 1 | 1 | 1 |  |  | 0.24988 | 102 | 8.7658 | 247
189 | 454 | NE | Ash | 454-15 | EOC |  |  |  | 3.7525 | 1.47 | 217 | 1 | 1 | 1 | 3 | 3 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 1 | 1 |  |  | 0.055161 | 231 | 39.1743 | 64
79 | 221 | NE | Santa Ysabel | P478409 | EOC |  |  |  | 23.4551 | 1.4698 | 218 | 1 | 3 | 0 | 1 | 2 | 0 | 1 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.34479 | 60 | 6.2673 | 270
214 | 522 | NE | Avocado | 522 | 522-25 |  |  |  | 5.5396 | 1.4599 | 219 | 1 | 2 | 2 | 1 | 1 | 0 | 2 | 3 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.080878 | 204 | 26.3558 | 98
198 | 502 | NE | Chicarita | 502-28 | EOC |  |  |  | 1.3011 | 1.45 | 220 | 1 | 1 | 1 | 3 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 | 2 | 2 |  |  | 0.018866 | 267 | 111.441 | 16
42 | 204 | OC | San Mateo | 204 | 204-24 | 204-2 | EOC |  | 6.3936 | 1.4499 | 221 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.092707 | 195 | 22.6791 | 118
85 | 230 | NE | Monserate | 230-4R | 230-133 |  |  |  | 7.039 | 1.4499 | 222 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.10207 | 190 | 20.5995 | 126
127 | 315 | OC | Capistrano | 315-2 | 315-502 |  |  |  | 5.84 | 1.4399 | 223 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 1 |  |  | 0.084095 | 201 | 24.6577 | 108
18 | 91 | EA | Jamacha | Z971734 | 91-649 |  |  |  | 0.84886 | 1.43 | 224 | 1 | 3 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 |  |  | 0.012139 | 274 | 168.4605 | 7
263 | 975 | NE | Creelman | 975 | 975-2 |  |  |  | 4.1525 | 1.43 | 225 | 1 | 2 | 1 | 1 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 2 | 2 |  |  | 0.05938 | 225 | 34.4374 | 71
33 | 185 | NE | Escondido | P417773 | EOC |  |  |  | 5.4458 | 1.4199 | 226 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.077331 | 207 | 26.075 | 100
312 | RC1 | NE | Reidy Canyon | RC1 | EOC |  |  |  | 2.6373 | 1.41 | 227 | 1 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 2 |  |  | 0.037186 | 246 | 53.4636 | 34
111 | 246 | EA | Los Coches | 246-11 | EOC |  |  |  | 9.2875 | 1.3999 | 228 | 1 | 1 | 2 | 1 | 1 | 0 | 3 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.13003 | 175 | 15.074 | 171
86 | 230 | NE | Monserate | 230-11 | EOC |  |  |  | 10.4443 | 1.3999 | 229 | 1 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 1 | 3 | 3 | 1 | 1 | 1 |  |  | 0.14622 | 161 | 13.4044 | 195
190 | 455 | NE | Ash | 455-979 | 455-34 | EOC |  |  | 4.0966 | 1.39 | 230 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 0.056943 | 229 | 33.9307 | 73
299 | FB1 | NE | Fallbrook 1 | FB1 | EOC |  |  |  | 4.1939 | 1.39 | 231 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 2 | 1 | 1 | 1 |  |  | 0.058296 | 227 | 33.1431 | 76
134 | 339 | OC | Cristianitos | 339 | EOC |  |  |  | 9.4475 | 1.3899 | 232 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 2 | 2 |  |  | 0.13132 | 173 | 14.7128 | 176
121 | 300 | NC | Pendleton | 300-1 | 300-25 | EOC |  |  | 11.622 | 1.3899 | 233 | 1 | 2 | 1 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 0.16155 | 155 | 11.9601 | 213
116 | 260 | CM | Otay Lakes | 260 | EOC |  |  |  | 12.5536 | 1.3899 | 234 | 1 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 2 | 1 | 0 | 3 | 0 | 2 | 1 | 3 | 3 |  |  | 0.1745 | 146 | 11.0725 | 224
40 | 202 | NC | Las Pulgas | 202 | EOC |  |  |  | 12.603 | 1.3899 | 235 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 0.17518 | 145 | 11.0291 | 225
309 | RA3 | NE | Ramona | RA3 | EOC |  |  |  | 3.068 | 1.38 | 236 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 0.042338 | 240 | 44.9806 | 54
188 | 452 | NE | Ash | 452-748 | EOC |  |  |  | 4.5273 | 1.38 | 237 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 2 | 1 |  |  | 0.062476 | 221 | 30.4819 | 80
130 | 329 | OC | San Mateo | 329 | EOC |  |  |  | 4.5527 | 1.38 | 238 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 2 | 1 |  |  | 0.062827 | 220 | 30.312 | 83
30 | 182 | NE | Escondido | 182-354 | P510606 | Z16125 | EOC |  | 10.4362 | 1.3799 | 239 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 2 | 1 | 1 | 3 | 2 | 1 | 1 | 3 |  |  | 0.14402 | 162 | 13.2232 | 198
300 | FB2 | NE | Fallbrook 2 | FB2 | EOC |  |  |  | 3.8405 | 1.37 | 240 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 0.052615 | 233 | 35.6722 | 68
234 | 728 | BC | Scripps | 728-689 | EOC |  |  |  | 2.086 | 1.36 | 241 | 1 | 1 | 0 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 0 | 3 | 1 | 3 | 1 |  |  | 0.028369 | 254 | 65.197 | 26
122 | 300 | NC | Pendleton | 300-25 | EOC |  |  |  | 5.5492 | 1.3599 | 242 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 0.07547 | 210 | 24.5078 | 109
216 | 523 | NE | Avocado | 523 | 523-31AE |  |  |  | 3.7097 | 1.35 | 243 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.05008 | 236 | 36.3915 | 66
270 | 1001 | NC | Rancho Santa Fe | P132166 | EOC |  |  |  | 2.1189 | 1.32 | 244 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 1 |  |  | 0.02797 | 255 | 62.2953 | 29
38 | 200 | OC | San Mateo | 200 | 200-29 | EOC |  |  | 3.1027 | 1.32 | 245 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 2 | 3 | 1 |  |  | 0.040955 | 242 | 42.5443 | 58
123 | 307 | NC | Rancho Santa Fe | P230241 | EOC |  |  |  | 0.7428 | 1.31 | 246 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 1 | 1 |  |  | 0.0097307 | 279 | 176.359 | 5
308 | RA2 | NE | Ramona | RA2 | EOC |  |  |  | 2.8767 | 1.31 | 247 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 0.037685 | 245 | 45.5382 | 52
43 | 204 | OC | San Mateo | 204-24 | EOC |  |  |  | 5.0672 | 1.3099 | 248 | 1 | 1 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.066381 | 218 | 25.8524 | 102
191 | 455 | NE | Ash | 455-926 | 455-34 | EOC |  |  | 1.7877 | 1.3 | 249 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 0 | 1 | 1 |  |  | 0.02324 | 262 | 72.7196 | 24
217 | 523 | NE | Avocado | 523-31AE | EOC |  |  |  | 2.7553 | 1.3 | 250 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.035819 | 250 | 47.1817 | 47
124 | 307 | NC | Rancho Santa Fe | Z12392 | EOC |  |  |  | 5.7 | 1.2899 | 251 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 2 |  |  | 0.07353 | 213 | 22.6316 | 119
283 | 1101 | NE | Artesian | 1101-1 | P819071 |  |  |  | 3.0506 | 1.28 | 252 | 1 | 2 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 3 | 1 |  |  | 0.039047 | 243 | 41.9594 | 60
49 | 209 | NC | Melrose | P214248 | EOC |  |  |  | 2.4578 | 1.25 | 253 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 2 | 1 | 1 |  |  | 0.030722 | 252 | 50.8592 | 35
132 | 331 | OC | San Mateo | 331-2 | EOC |  |  |  | 2.8953 | 1.25 | 254 | 1 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 1 |  |  | 0.036191 | 248 | 43.1739 | 57
112 | 247 | EA | Los Coches | 247-14 | P33699 |  |  |  | 5.5227 | 1.2399 | 255 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 3 | 2 | 2 | 1 | 1 |  |  | 0.068482 | 217 | 22.4527 | 121
34 | 188 | NE | Escondido | P216702 | EOC |  |  |  | 0.9428 | 1.23 | 256 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 1 | 1 |  |  | 0.011596 | 275 | 130.462 | 12
222 | 536 | CM | Border | Z135595 | EOC |  |  |  | 3.3883 | 1.23 | 257 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 1 | 1 | 1 | 2 | 3 |  |  | 0.041676 | 241 | 36.3018 | 67
89 | 232 | NE | Monserate | 232 | EOC |  |  |  | 4.967 | 1.21 | 258 | 1 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.060101 | 223 | 24.3606 | 110
221 | 527 | OC | Las Pulgas | 527 | EOC |  |  |  | 6.2663 | 1.1899 | 259 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3 | 3 |  |  | 0.074569 | 211 | 18.9905 | 136
37 | 198 | NC | San Luis Rey | 198-4 | P121327 | Z29143 |  |  | 0.48769 | 1.18 | 260 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 3 | 3 |  |  | 0.0057547 | 283 | 241.9573 | 2
133 | 338 | OC | Cristianitos | 338 | EOC |  |  |  | 0.91439 | 1.18 | 261 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 1 |  |  | 0.01079 | 276 | 129.0472 | 13
224 | 542 | NE | Bernardo | 542 | 542-13 |  |  |  | 1.8415 | 1.18 | 262 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 2 | 2 |  |  | 0.021729 | 264 | 64.079 | 28
237 | 791 | NE | Felicita | 791-26 | EOC |  |  |  | 4.943 | 1.18 | 263 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 0 | 3 | 0 | 2 | 1 |  |  | 0.058327 | 226 | 23.8722 | 113
282 | 1100 | NE | Artesian | P515154 | EOC |  |  |  | 1.2008 | 1.17 | 264 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 0.014049 | 272 | 97.4385 | 17
36 | 197 | OC | Capistrano | 197-19 | EOC |  |  |  | 1.4297 | 1.17 | 265 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 3 | 2 |  |  | 0.016728 | 271 | 81.8334 | 21
281 | 1100 | NE | Artesian | 1100 | 1100-46 | EOC |  |  | 2.458 | 1.17 | 266 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 3 | 1 |  |  | 0.028758 | 253 | 47.6006 | 46
31 | 182 | NE | Escondido | P510606 | P810041 | P113377 | EOC |  | 6.4737 | 1.1699 | 267 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.075742 | 209 | 18.0732 | 148
39 | 200 | OC | San Mateo | 200-28 | 200-6 | 200-438 |  |  | 0.4553 | 1.12 | 268 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 3 | 2 | 1 | 1 |  |  | 0.0050994 | 286 | 245.99 | 1
48 | 206 | NC | Melrose | 206-1105 | EOC |  |  |  | 4.8136 | 1.12 | 269 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 3 | 2 | 1 | 1 | 1 |  |  | 0.053913 | 232 | 23.2672 | 116
128 | 315 | OC | Capistrano | 315-501 | EOC |  |  |  | 0.47576 | 1.11 | 270 | 1 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 2 |  |  | 0.0052809 | 284 | 233.3121 | 3
223 | 540 | NE | Bernardo | 540 | 540-2 |  |  |  | 0.95871 | 1.11 | 271 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 2 | 1 |  |  | 0.010642 | 277 | 115.7803 | 15
106 | 242 | EA | Los Coches | 242 | 241-T6-242 |  |  |  | 2.3888 | 1.11 | 272 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 1 |  |  | 0.026516 | 258 | 46.4663 | 51
249 | 970 | NE | Creelman | 970 | 970-10 |  |  |  | 2.2697 | 1.09 | 273 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 2 | 0 | 3 | 2 |  |  | 0.02474 | 259 | 48.024 | 43
32 | 185 | NE | Escondido | P114604 | EOC |  |  |  | 0.88409 | 1.08 | 274 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.0095482 | 280 | 122.1594 | 14
107 | 242 | EA | Los Coches | P970731 | EOC |  |  |  | 1.7996 | 1.08 | 275 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.019436 | 265 | 60.0126 | 31
115 | 252 | BC | Kearny | P36981 | EOC |  |  |  | 4.1129 | 1.08 | 276 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 1 | 3 | 3 | 3 |  |  | 0.044419 | 239 | 26.259 | 99
236 | 776 | BC | Mesa Heights | 776-8 | EOC |  |  |  | 2.1811 | 1.07 | 277 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 3 | 1 |  |  | 0.023337 | 261 | 49.0587 | 38
229 | 594 | CM | Proctor Valley | P166873 | EOC |  |  |  | 1.8324 | 1.06 | 278 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 3 | 0 | 2 | 0 | 3 | 1 |  |  | 0.019423 | 266 | 57.8481 | 32
41 | 203 | OC | San Mateo | 203 | 203-7 |  |  |  | 2.5756 | 1.06 | 279 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 1 | 1 |  |  | 0.027301 | 257 | 41.156 | 62
47 | 205 | NC | Melrose | P116036 | EOC |  |  |  | 0.4911 | 1.04 | 280 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 1 |  |  | 0.0051074 | 285 | 211.7702 | 4
313 | SE4 | OC | Serra | SE4 | EOC |  |  |  | 0.59299 | 1.03 | 281 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 1 |  |  | 0.0061078 | 282 | 173.6953 | 6
248 | 968 | BC | Eastgate | 968-14 | EOC |  |  |  | 2.1536 | 1.03 | 282 | 1 | 1 | 0 | 2 | 2 | 1 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 |  |  | 0.022182 | 263 | 47.8269 | 44
46 | 205 | NC | Melrose | P111778 | EOC |  |  |  | 0.70625 | 0.95999 | 283 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 1 |  |  | 0.00678 | 281 | 135.9292 | 10
235 | 770 | BC | Mesa Heights | Z90080 | EOC |  |  |  | 1.8898 | 0.93998 | 284 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3 | 1 |  |  | 0.017764 | 268 | 49.7414 | 37
192 | 463 | CM | San Ysidro | P108483 | EOC |  |  |  | 1.9051 | 0.92998 | 285 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 1 |  |  | 0.017718 | 269 | 48.816 | 39
131 | 330 | OC | San Mateo | 330-10 | P25224 |  |  |  | 1.4953 | 0.67999 | 286 | 1 | 2 | 1 | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  |  | 0.010168 | 278 | 45.4769 | 53
| A | Circuit | bar: Environment 1
| B | Study segment boundaries | bar: Environment 1
| C | Length in miles of the study segment | bar: Environment 1
| D | Weighted score | bar: Environment 1
| E | Ranking | bar: Environment 1
| 1 | Risk zone: HRFA: 3, FTZ: 1
| 2 | Wind Factor: Based on the forecasted frequency of extreme wind events - (Brian D'Agostino)
| 3 | Tree Factor: Density of trees in proximity that are >=40ft weighted by species (Vegetation Management)
| 4 | Fuel: (Fire Coordinator)
| 5 | Fire ignition risk: (Fire Coordinator)
| 6 | Capacitor factor - number of capacitors in segment (TDAM) | bar: Environment 1
| 7 | Expulsion fuse factor (TDAM) | bar: Environment 1
| 8 | Switch factor (TDAM) | bar: Environment 1
| 9 | Conductor factor -smaller than 2/0- (TDAM) | bar: Environment 1
| 10 | Transformer factor (TDAM) | bar: Environment 1
| 11 | High-risk transformer factor (TDAM) | bar: Environment 1
| 12 | Ranking by district operating center | bar: Environment 1
| 13 | 5-Year Outage History Index (TDAM) | bar: Environment 1
| 14 | Relative structure value in projected burn path (Fire Coordinator) | bar: Environment 1
| 15 | Reduction in the number of customers impacted by 2012 safety shut off plan (TDAM) | bar: Environment 1
| 16 | Service to critical facilities, water, communication, health, public protection (TDAM, CISCO) | bar: Environment 1
| 17 | Ranking by environmental | bar: Environment 1
| 18 | Ranking by cultural | bar: Environment 1
Italic = open switch (tie or fuse bypass)

## ScroreDist Regression
SUMMARY OUTPUT
Regression Statistics
Multiple R | 0.61453
R Square | 0.37765
Adjusted R Square | 0.37545
Standard Error | 8.0371
Observations | 286
ANOVA
| df | SS | MS | F | Significance F
Regression | 1 | 11131.7549 | 11131.7549 | 172.3319 | 4.3372e-31
Residual | 284 | 18344.9379 | 64.5949
Total | 285 | 29476.6927
| Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
Intercept | -18.5465 | 2.3875 | -7.7681 | 1.461e-13 | -23.2459 | -13.847 | -23.2459 | -13.847
X Variable 1 | 17.5436 | 1.3364 | 13.1275 | 4.3372e-31 | 14.9131 | 20.1741 | 14.9131 | 20.1741

## AltMatrix1
| Study Segment | [8 empty] | Results |  | Ignition Risk | [12 empty] | Impact
[12 empty] | Environment |  |  |  |  | System | [17 empty] | Risk Class | Class Frc
| A | A1 | A2 | B | B1 | B2 | B3 | B4 | C | D | E | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 17 | 18 | Totals | Shutoff |  |  |  |  | Environment | 52% | 52% |  |  | 30% |  |  | 35% |  |  | 70%
| 96% | [10 empty] | 8% | 12% | 10% | 12% | 10% | 3% | 3% | 2% | 2% | 2% | 2% | 4% | 5% | 12% | 3% | 3% | 3% | 96% | 4% |  |  |  |  | System | 23% | 23% |  |  | 50% |  |  | 25% |  |  | 15%
ndx | Ckt | Op Dist | Sub | Section Start | Section End | Section End | Section End | Section End | Dist (Mi) | Score | Rank | Zone | Wind | Tree | Fuel | Fire Ign. Risk | Cap | Exp Fuse | SWs | Cond | Trans (All) | HR Trans | DOC Rank | Rel Hist | Value Risk | Crit Svc | Bio Rank | Cult Rank |  | Shutoff | DstMlt Score | DstMlt Rank | DstDiv Score | DstDiv Rank | Impact | 25% | 25% |  |  | 20% |  |  | 40% |  |  | 15%
76 | 221 | NE | Santa Ysabel | 221-33R | 221-14 |  |  |  | 28.2432 | 2.5197 | 1 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.71173 | 17 | 8.9225 | 246 |  |  | 2.5197 | 1 | 0 | 2.5333 | 1 | 0 | 2.2625 | 1 | 0 | 2.7086 | 1 | 0
168 | 442 | EA | Glencliff | 442-2R | 442-16R | EOC |  |  | 15.3869 | 2.4598 | 2 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 0.37852 | 52 | 15.9876 | 158 |  |  | 2.4598 | 2 | 0 | 2.2793 | 9 | 7 | 2.2436 | 2 | 0 | 2.6649 | 2 | 0
98 | 237 | NE | Creelman | P117100 | EOC |  |  |  | 31.21 | 2.3197 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 2 | 3 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.72407 | 16 | 7.4335 | 258 |  |  | 2.3197 | 3 | 0 | 2.2221 | 13 | 10 | 1.9989 | 42 | 39 | 2.5828 | 3 | 0
82 | 222 | NE | Santa Ysabel | 222-8 | EOC |  |  |  | 38.3066 | 2.3196 | 4 | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 0.88871 | 6 | 6.0564 | 273 |  |  | 2.3196 | 4 | 0 | 2.3313 | 7 | 3 | 2.0793 | 17 | 13 | 2.4963 | 5 | 1
276 | 1030 | NE | Valley Center | 1030-14 | 1030-20R |  |  |  | 40.054 | 2.3196 | 5 | 3 | 2 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 2 | 1 | 1 | 3 |  |  | 0.92925 | 5 | 5.7922 | 276 |  |  | 2.3196 | 5 | 0 | 2.2076 | 16 | 11 | 2.1254 | 10 | 5 | 2.4916 | 6 | 1
57 | 212 | NE | Warners | P19585 | EOC |  |  |  | 23.0977 | 2.3098 | 6 | 3 | 3 | 3 | 3 | 3 | 0 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 1 | 0 | 2 | 3 |  |  | 0.53356 | 28 | 10.001 | 235 |  |  | 2.3098 | 6 | 0 | 2.1592 | 22 | 16 | 2.0035 | 38 | 32 | 2.5748 | 4 | 2
163 | 440 | EA | Glencliff | 440-6 | EOC |  |  |  | 12.2689 | 2.2899 | 7 | 3 | 2 | 3 | 3 | 3 | 0 | 2 | 2 | 2 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 0.28096 | 88 | 18.665 | 139 |  |  | 2.2899 | 7 | 0 | 2.0602 | 42 | 35 | 2.1239 | 11 | 4 | 2.4692 | 8 | 1
206 | 520 | NE | Avocado | 520-33R | 520-1053 |  |  |  | 25.2805 | 2.2897 | 8 | 3 | 3 | 3 | 2 | 3 | 0 | 2 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.57892 | 24 | 9.0584 | 243 |  |  | 2.2897 | 8 | 0 | 2.1837 | 18 | 10 | 2.0776 | 19 | 11 | 2.4738 | 7 | 1
251 | 971 | NE | Creelman | 971 | 971-26R |  |  |  | 59.9191 | 2.2894 | 9 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 1.3721 | 1 | 3.8218 | 286 |  |  | 2.2894 | 9 | 0 | 2.3431 | 5 | 4 | 2.1186 | 12 | 3 | 2.404 | 14 | 5
292 | 1233 | NE | Pala | 1233-252R | EOC |  |  |  | 22.833 | 2.2798 | 10 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 0.52059 | 31 | 9.9856 | 237 |  |  | 2.2798 | 10 | 0 | 2.1981 | 17 | 7 | 2.1543 | 6 | 4 | 2.3932 | 15 | 5
277 | 1030 | NE | Valley Center | 1030-20R | EOC |  |  |  | 32.6343 | 2.2797 | 11 | 3 | 2 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 1 | 3 | 2 | 2 | 1 | 1 | 3 |  |  | 0.74406 | 13 | 6.9865 | 263 |  |  | 2.2797 | 11 | 0 | 2.1207 | 28 | 17 | 2.082 | 15 | 4 | 2.4656 | 10 | 1
253 | 971 | NE | Creelman | 971-24 | 971-306R | EOC |  |  | 21.5348 | 2.2698 | 12 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.48884 | 33 | 10.5411 | 228 |  |  | 2.2698 | 12 | 0 | 2.3412 | 6 | 6 | 2.0819 | 16 | 4 | 2.3929 | 16 | 4
95 | 236 | NE | Creelman | 236 | EOC |  |  |  | 45.9146 | 2.2695 | 13 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 1.0423 | 3 | 4.944 | 282 |  |  | 2.2695 | 13 | 0 | 2.4141 | 2 | 11 | 2.0745 | 20 | 7 | 2.3804 | 17 | 4
180 | 448 | EA | Cameron | 448-6 | 448-13R | 448-11R |  |  | 8.9731 | 2.2599 | 14 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.20279 | 132 | 25.1864 | 104 |  |  | 2.2599 | 14 | 0 | 2.0455 | 46 | 32 | 2.0523 | 23 | 9 | 2.4667 | 9 | 5
151 | 357 | EA | Alpine | 357 | 357-45R |  |  |  | 11.8898 | 2.2499 | 15 | 3 | 2 | 3 | 2 | 3 | 0 | 3 | 3 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.26752 | 96 | 18.9238 | 137 |  |  | 2.2499 | 15 | 0 | 2.1649 | 20 | 5 | 2.1301 | 9 | 6 | 2.3598 | 21 | 6
3 | 73 | EA | Descanso | 73 | 73-49R |  |  |  | 12.8051 | 2.2399 | 16 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 3 | 2 | 2 | 1 | 2 | 2 |  |  | 0.28683 | 82 | 17.493 | 151 |  |  | 2.2399 | 16 | 0 | 2.002 | 58 | 42 | 2.0305 | 25 | 9 | 2.4536 | 11 | 5
155 | 358 | EA | Alpine | 358-14 | EOC |  |  |  | 17.9513 | 2.2398 | 17 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 3 |  |  | 0.40211 | 44 | 12.4782 | 209 |  |  | 2.2398 | 17 | 0 | 2.2204 | 14 | 3 | 2.1913 | 4 | 13 | 2.2807 | 42 | 25
74 | 220 | NE | Santa Ysabel | P212213 | EOC |  |  |  | 33.3369 | 2.2297 | 18 | 3 | 3 | 2 | 3 | 3 | 0 | 2 | 1 | 3 | 2 | 2 | 3 | 2 | 2 | 0 | 1 | 2 |  |  | 0.74341 | 14 | 6.6893 | 267 |  |  | 2.2297 | 18 | 0 | 2.0625 | 39 | 21 | 1.9886 | 47 | 29 | 2.45 | 12 | 6
81 | 222 | NE | Santa Ysabel | 222-1370R | EOC |  |  |  | 51 | 2.2295 | 19 | 3 | 3 | 2 | 2 | 3 | 1 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 1.1373 | 2 | 4.3725 | 285 |  |  | 2.2295 | 19 | 0 | 2.2952 | 8 | 11 | 2.0227 | 31 | 12 | 2.3681 | 19 | 0
63 | 214 | NE | Rincon | 214-7 | 214-538 | EOC |  |  | 32.9292 | 2.2197 | 20 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 3 | 3 | 1 |  |  | 0.73103 | 15 | 6.7417 | 266 |  |  | 2.2197 | 20 | 0 | 2.2592 | 10 | 10 | 2.1387 | 7 | 13 | 2.2707 | 44 | 24
77 | 221 | NE | Santa Ysabel | 221-14 | P519130 | P478409 |  |  | 16.0578 | 2.2098 | 21 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 1 | 3 | 3 | 2 | 1 | 3 | 3 |  |  | 0.35488 | 58 | 13.7628 | 189 |  |  | 2.2098 | 21 | 0 | 2.014 | 54 | 33 | 2.07 | 21 | 0 | 2.3615 | 20 | 1
219 | 524 | EA | Jamacha | 524-13 | 524-34 |  |  |  | 38.5665 | 2.2096 | 22 | 3 | 1 | 3 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.85232 | 7 | 5.7304 | 277 |  |  | 2.2096 | 22 | 0 | 2.3878 | 3 | 19 | 2.1928 | 3 | 19 | 2.1793 | 70 | 48
153 | 357 | EA | Alpine | 357-750R | EOC |  |  |  | 7.1138 | 2.1999 | 23 | 3 | 2 | 3 | 2 | 3 | 0 | 3 | 0 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.1565 | 159 | 30.9257 | 79 |  |  | 2.1999 | 23 | 0 | 2.015 | 53 | 30 | 2.0912 | 13 | 10 | 2.3257 | 30 | 7
152 | 357 | EA | Alpine | 357-45R | 357-750R |  |  |  | 9.7472 | 2.1999 | 24 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.21444 | 126 | 22.5707 | 120 |  |  | 2.1999 | 24 | 0 | 2.1747 | 19 | 5 | 2.1325 | 8 | 16 | 2.2563 | 46 | 22
27 | 176 | NE | Poway | 176-26R | EOC |  |  |  | 36.4856 | 2.1996 | 25 | 3 | 1 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 2 |  |  | 0.80268 | 9 | 6.0298 | 274 |  |  | 2.1996 | 25 | 0 | 2.3661 | 4 | 21 | 2.1819 | 5 | 20 | 2.1728 | 73 | 48
257 | 972 | NE | Creelman | P13262 | EOC |  |  |  | 15.6979 | 2.1898 | 26 | 3 | 2 | 2 | 3 | 3 | 1 | 2 | 0 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 1 |  |  | 0.34378 | 61 | 13.9509 | 187 |  |  | 2.1898 | 26 | 0 | 2.0849 | 34 | 8 | 2.0258 | 28 | 2 | 2.3377 | 28 | 2
4 | 73 | EA | Descanso | 73-49R | 73-23R |  |  |  | 23.0691 | 2.1898 | 27 | 3 | 3 | 1 | 3 | 3 | 1 | 2 | 2 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 |  |  | 0.50521 | 32 | 9.4932 | 241 |  |  | 2.1898 | 27 | 0 | 2.0941 | 32 | 5 | 2.002 | 39 | 12 | 2.3531 | 22 | 5
182 | 448 | EA | Cameron | 448-13R | 448-15R |  |  |  | 12.7725 | 2.1799 | 28 | 3 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 0.27844 | 91 | 17.0679 | 155 |  |  | 2.1799 | 28 | 0 | 2.0313 | 48 | 20 | 2.0066 | 36 | 8 | 2.3451 | 24 | 4
103 | 240 | EA | Los Coches | 240 | 240-1097R | 240-1095R |  |  | 13.9318 | 2.1699 | 29 | 3 | 1 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.30232 | 75 | 15.5759 | 165 |  |  | 2.1699 | 29 | 0 | 2.1558 | 23 | 6 | 1.9815 | 50 | 21 | 2.3139 | 33 | 4
183 | 448 | EA | Cameron | 448-15R | EOC |  |  |  | 14.9491 | 2.1699 | 30 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.32439 | 67 | 14.516 | 179 |  |  | 2.1699 | 30 | 0 | 2.0095 | 55 | 25 | 1.9958 | 44 | 14 | 2.3385 | 26 | 4
179 | 448 | EA | Cameron | 448 | 448-6 |  |  |  | 17.3138 | 2.1698 | 31 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.37571 | 53 | 12.5333 | 205 |  |  | 2.1698 | 31 | 0 | 2.0095 | 56 | 25 | 1.9957 | 45 | 14 | 2.3385 | 27 | 4
181 | 448 | EA | Cameron | 448-11R | EOC |  |  |  | 26.1881 | 2.1697 | 32 | 3 | 3 | 1 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.56828 | 26 | 8.2862 | 252 |  |  | 2.1697 | 32 | 0 | 2.0506 | 44 | 12 | 1.9803 | 51 | 19 | 2.34 | 25 | 7
70 | 217 | NE | Rincon | 217 | 217-835R |  |  |  | 45.561 | 2.1695 | 33 | 3 | 3 | 3 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 3 |  |  | 0.98867 | 4 | 4.7628 | 283 |  |  | 2.1695 | 33 | 0 | 2.2328 | 12 | 21 | 2.0534 | 22 | 11 | 2.2411 | 51 | 18
162 | 440 | EA | Glencliff | 440 | 440-6 |  |  |  | 8.0581 | 2.1599 | 34 | 3 | 2 | 2 | 3 | 3 | 0 | 1 | 2 | 2 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 0.17406 | 147 | 26.8052 | 96 |  |  | 2.1599 | 34 | 0 | 1.9373 | 75 | 41 | 2.024 | 30 | 4 | 2.3151 | 32 | 2
169 | 442 | EA | Glencliff | 442-16R | EOC |  |  |  | 10.7032 | 2.1599 | 35 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 1 | 1 | 3 | 3 |  |  | 0.23119 | 116 | 20.1808 | 129 |  |  | 2.1599 | 35 | 0 | 1.9105 | 82 | 47 | 1.9128 | 67 | 32 | 2.4046 | 13 | 22
154 | 358 | EA | Alpine | 358 | 358-14 |  |  |  | 11.2472 | 2.1599 | 36 | 3 | 2 | 2 | 2 | 3 | 0 | 3 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.24294 | 108 | 19.2048 | 134 |  |  | 2.1599 | 36 | 0 | 2.0877 | 33 | 3 | 2.089 | 14 | 22 | 2.2302 | 54 | 18
202 | 520 | NE | Avocado | 520-35R | 520-11 |  |  |  | 13.8597 | 2.1599 | 37 | 3 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 1 | 2 | 0 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.29937 | 77 | 15.5848 | 163 |  |  | 2.1599 | 37 | 0 | 2.0609 | 40 | 3 | 1.9778 | 52 | 15 | 2.3197 | 31 | 6
220 | 524 | EA | Jamacha | 524-34 | EOC |  |  |  | 30.2254 | 2.1497 | 38 | 3 | 1 | 2 | 3 | 3 | 0 | 2 | 0 | 2 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.64985 | 20 | 7.1132 | 262 |  |  | 2.1497 | 38 | 0 | 2.0658 | 38 | 0 | 2.078 | 18 | 20 | 2.2235 | 56 | 18
21 | 157 | EA | Barrett | 157-75R | EOC |  |  |  | 34.9093 | 2.1397 | 39 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.74706 | 12 | 6.1302 | 271 |  |  | 2.1397 | 39 | 0 | 2.2089 | 15 | 24 | 2.0055 | 37 | 2 | 2.2232 | 57 | 18
254 | 971 | NE | Creelman | 971-306R | EOC |  |  |  | 17.7968 | 2.1298 | 40 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.37907 | 51 | 11.9685 | 212 |  |  | 2.1298 | 40 | 0 | 1.9957 | 61 | 21 | 1.9451 | 57 | 17 | 2.3001 | 38 | 2
101 | 239 | NE | Pala | 239-15R | EOC |  |  |  | 18.8278 | 2.1298 | 41 | 3 | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 3 |  |  | 0.40103 | 46 | 11.313 | 220 |  |  | 2.1298 | 41 | 0 | 2.1049 | 31 | 10 | 2.0256 | 29 | 12 | 2.2137 | 59 | 18
201 | 520 | NE | Avocado | 520-26AE | 520-35R |  |  |  | 10.4591 | 2.1199 | 42 | 3 | 2 | 2 | 2 | 3 | 1 | 2 | 1 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 2 |  |  | 0.22173 | 122 | 20.2694 | 128 |  |  | 2.1199 | 42 | 0 | 2.0832 | 35 | 7 | 2.0148 | 33 | 9 | 2.2072 | 60 | 18
140 | 351 | NE | Lilac | 351 | 351-819R |  |  |  | 10.6801 | 2.1199 | 43 | 3 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 0.22642 | 120 | 19.85 | 132 |  |  | 2.1199 | 43 | 0 | 2.042 | 47 | 4 | 2.0302 | 26 | 17 | 2.2057 | 61 | 18
144 | 353 | NE | Lilac | 353-914R | EOC |  |  |  | 12.115 | 2.1199 | 44 | 3 | 2 | 3 | 2 | 3 | 1 | 3 | 2 | 1 | 2 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.25684 | 98 | 17.499 | 150 |  |  | 2.1199 | 44 | 0 | 2.0472 | 45 | 1 | 1.9272 | 61 | 17 | 2.2813 | 41 | 3
185 | 449 | EA | Cameron | 449-13R | EOC |  |  |  | 13.7621 | 2.1199 | 45 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 1 | 2 |  |  | 0.29176 | 80 | 15.4046 | 167 |  |  | 2.1199 | 45 | 0 | 1.8236 | 110 | 65 | 1.8693 | 78 | 33 | 2.3785 | 18 | 27
290 | 1215 | EA | Crestwood | 1215 | EOC |  |  |  | 21.9858 | 2.1198 | 46 | 3 | 3 | 1 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 0 | 2 | 3 | 1 | 1 | 3 | 3 |  |  | 0.4661 | 35 | 9.6426 | 240 |  |  | 2.1198 | 46 | 0 | 1.9832 | 64 | 18 | 1.9106 | 68 | 22 | 2.309 | 34 | 12
73 | 220 | NE | Santa Ysabel | 220-294R | P212213 |  |  |  | 11.5263 | 2.1099 | 47 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 2 | 2 | 0 | 3 | 3 |  |  | 0.24321 | 107 | 18.3059 | 143 |  |  | 2.1099 | 47 | 0 | 1.8379 | 100 | 53 | 1.946 | 55 | 8 | 2.2979 | 39 | 8
294 | 1250 | NE | Olivenhain | 1250 | 1250-9 |  |  |  | 15.9405 | 2.1098 | 48 | 1 | 2 | 3 | 3 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 0.33635 | 62 | 13.2367 | 197 |  |  | 2.1098 | 48 | 0 | 1.9244 | 77 | 29 | 1.9944 | 46 | 2 | 2.2407 | 52 | 4
5 | 73 | EA | Descanso | 73-23R | EOC |  |  |  | 18.0922 | 2.1098 | 49 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 |  |  | 0.38175 | 50 | 11.6625 | 216 |  |  | 2.1098 | 49 | 0 | 1.9203 | 78 | 29 | 1.9151 | 65 | 16 | 2.3009 | 36 | 13
278 | 1039 | NE | Ash | 1039-13AE | EOC |  |  |  | 13.2862 | 2.0999 | 50 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 2 | 3 | 1 | 1 | 1 |  |  | 0.27901 | 90 | 15.8059 | 160 |  |  | 2.0999 | 50 | 0 | 1.9985 | 59 | 9 | 2.0084 | 35 | 15 | 2.1926 | 63 | 13
23 | 157 | EA | Barrett | 157-87R | EOC |  |  |  | 33.3 | 2.0997 | 51 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.6993 | 18 | 6.3063 | 269 |  |  | 2.0997 | 51 | 0 | 2.1219 | 27 | 24 | 1.962 | 54 | 3 | 2.1971 | 62 | 11
240 | 907 | NE | Valley Center | 907 | 907-45 |  |  |  | 11.4294 | 2.0899 | 52 | 3 | 2 | 3 | 2 | 2 | 0 | 3 | 2 | 1 | 2 | 2 | 3 | 2 | 2 | 3 | 1 | 2 |  |  | 0.23887 | 110 | 18.2862 | 144 |  |  | 2.0899 | 52 | 0 | 2.018 | 52 | 0 | 1.9822 | 49 | 3 | 2.1877 | 65 | 13
148 | 355 | EA | Alpine | 355 | EOC |  |  |  | 13.5146 | 2.0899 | 53 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 0 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 0.28245 | 85 | 15.4648 | 166 |  |  | 2.0899 | 53 | 0 | 1.9768 | 67 | 14 | 1.9975 | 43 | 10 | 2.1861 | 67 | 14
241 | 907 | NE | Valley Center | 907-45 | EOC |  |  |  | 6.8528 | 2.0799 | 54 | 3 | 2 | 2 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 2 |  |  | 0.14254 | 164 | 30.3524 | 82 |  |  | 2.0799 | 54 | 0 | 1.8047 | 114 | 60 | 1.9217 | 64 | 10 | 2.2645 | 45 | 9
149 | 356 | EA | Alpine | 356 | 356-19R |  |  |  | 12.1782 | 2.0799 | 55 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 0.25331 | 100 | 17.0797 | 154 |  |  | 2.0799 | 55 | 0 | 1.955 | 68 | 13 | 1.9867 | 48 | 7 | 2.1796 | 69 | 14
80 | 222 | NE | Santa Ysabel | 222 | 222-1370R | 222-8 |  |  | 14.6 | 2.0799 | 56 | 3 | 3 | 2 | 1 | 3 | 0 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 0.30368 | 74 | 14.2466 | 183 |  |  | 2.0799 | 56 | 0 | 2.1611 | 21 | 35 | 1.9097 | 69 | 13 | 2.1874 | 66 | 10
203 | 520 | NE | Avocado | 520-11 | 520-1054 | EOC |  |  | 15.9606 | 2.0798 | 57 | 3 | 2 | 3 | 2 | 3 | 0 | 1 | 1 | 1 | 2 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.33198 | 63 | 13.0321 | 201 |  |  | 2.0798 | 57 | 0 | 1.9189 | 79 | 22 | 1.8991 | 72 | 15 | 2.2536 | 47 | 10
25 | 175 | NE | Poway | 175-90R | EOC |  |  |  | 20.7559 | 2.0798 | 58 | 3 | 2 | 2 | 2 | 2 | 1 | 3 | 2 | 1 | 3 | 0 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 0.43172 | 43 | 10.0213 | 234 |  |  | 2.0798 | 58 | 0 | 2.1146 | 30 | 28 | 2.028 | 27 | 31 | 2.1101 | 86 | 28
96 | 237 | NE | Creelman | 237 | 237-8 |  |  |  | 29.9326 | 2.0797 | 59 | 3 | 3 | 3 | 1 | 2 | 1 | 3 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.6226 | 22 | 6.949 | 264 |  |  | 2.0797 | 59 | 0 | 2.1197 | 29 | 30 | 1.9249 | 62 | 3 | 2.1857 | 68 | 9
167 | 442 | EA | Glencliff | 442 | 442-2R | EOC |  |  | 2.4383 | 2.07 | 60 | 3 | 3 | 1 | 3 | 3 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 3 | 2 |  |  | 0.050472 | 235 | 84.8967 | 19 |  |  | 2.07 | 60 | 0 | 1.751 | 142 | 82 | 1.9026 | 71 | 11 | 2.2719 | 43 | 17
288 | 1166 | EA | Loveland | 1166-18R | 1166-1 | EOC |  |  | 8.3159 | 2.0699 | 61 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 0.17214 | 148 | 24.892 | 105 |  |  | 2.0699 | 61 | 0 | 1.7561 | 138 | 77 | 1.7996 | 99 | 38 | 2.3475 | 23 | 38
97 | 237 | NE | Creelman | 237-8 | P117100 | EOC |  |  | 14.7367 | 2.0699 | 62 | 3 | 3 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 3 | 1 |  |  | 0.30505 | 73 | 14.0465 | 185 |  |  | 2.0699 | 62 | 0 | 1.9838 | 63 | 1 | 1.9367 | 59 | 3 | 2.19 | 64 | 2
20 | 157 | EA | Barrett | 157-77R | EOC |  |  |  | 40.857 | 2.0696 | 63 | 3 | 3 | 2 | 1 | 2 | 0 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 0.84574 | 8 | 5.0665 | 281 |  |  | 2.0696 | 63 | 0 | 2.1339 | 25 | 38 | 2.0015 | 40 | 23 | 2.1049 | 89 | 26
291 | 1233 | NE | Pala | 1233 | 1233-252R |  |  |  | 4.9167 | 2.06 | 64 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 2 | 1 |  |  | 0.10128 | 191 | 41.8983 | 61 |  |  | 2.06 | 64 | 0 | 1.8385 | 99 | 35 | 1.9721 | 53 | 11 | 2.1789 | 71 | 7
66 | 214 | NE | Rincon | 214-16 | EOC |  |  |  | 6.7678 | 2.0599 | 65 | 3 | 3 | 2 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 3 | 2 | 3 |  |  | 0.13942 | 167 | 30.4382 | 81 |  |  | 2.0599 | 65 | 0 | 1.6787 | 156 | 91 | 1.9307 | 60 | 5 | 2.2483 | 49 | 16
243 | 908 | NE | Valley Center | 908-23 | EOC |  |  |  | 30.1309 | 2.0597 | 66 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.6207 | 23 | 6.8368 | 265 |  |  | 2.0597 | 66 | 0 | 2.0762 | 36 | 30 | 1.9032 | 70 | 4 | 2.1726 | 74 | 8
146 | 354 | NE | Lilac | 354-5 | 354-24AE | EOC |  |  | 36.9813 | 2.0596 | 67 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 3 | 1 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 0.76181 | 11 | 5.5704 | 278 |  |  | 2.0596 | 67 | 0 | 2.2493 | 11 | 56 | 2.0001 | 41 | 26 | 2.0584 | 104 | 37
262 | 974 | NE | Creelman | 974-7 | EOC |  |  |  | 15.2072 | 2.0498 | 68 | 3 | 2 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 3 | 3 |  |  | 0.31175 | 70 | 13.4805 | 194 |  |  | 2.0498 | 68 | 0 | 1.8578 | 94 | 26 | 1.9458 | 56 | 12 | 2.1739 | 72 | 4
305 | OK1 | NE | Oaks 1 | OK1 | EOC |  |  |  | 8.3875 | 2.0399 | 69 | 3 | 3 | 2 | 3 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | 0.1711 | 149 | 24.3219 | 111 |  |  | 2.0399 | 69 | 0 | 1.6909 | 153 | 84 | 1.767 | 112 | 43 | 2.3279 | 29 | 40
289 | 1166 | EA | Loveland | 1166-1 | EOC |  |  |  | 10.6926 | 2.0399 | 70 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 2 |  |  | 0.21813 | 123 | 19.0786 | 135 |  |  | 2.0399 | 70 | 0 | 1.8001 | 116 | 46 | 1.8474 | 84 | 14 | 2.2415 | 50 | 20
160 | 411 | EA | Granite | 411-14R | 411-8 |  |  |  | 17.7886 | 2.0398 | 71 | 1 | 1 | 3 | 2 | 3 | 3 | 3 | 2 | 2 | 3 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.36289 | 54 | 11.468 | 218 |  |  | 2.0398 | 71 | 0 | 2.1555 | 24 | 47 | 2.0176 | 32 | 39 | 2.0285 | 117 | 46
55 | 211 | NE | Warners | 211-262R | EOC |  |  |  | 17.1311 | 2.0298 | 72 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 1 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 0.34776 | 59 | 11.8498 | 214 |  |  | 2.0298 | 72 | 0 | 1.87 | 92 | 20 | 1.782 | 105 | 33 | 2.2535 | 48 | 24
232 | 599 | NE | San Marcos | P116474 | 599-1181 | EOC |  |  | 17.6703 | 2.0298 | 73 | 1 | 1 | 3 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 2 | 2 | 3 | 1 | 1 | 2 |  |  | 0.35871 | 56 | 11.4882 | 217 |  |  | 2.0298 | 73 | 0 | 2.0606 | 41 | 32 | 2.0139 | 34 | 39 | 2.0343 | 116 | 43
186 | 449 | EA | Cameron | 449-1 | EOC |  |  |  | 5.9386 | 2.0199 | 74 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 0 | 3 | 3 |  |  | 0.11996 | 181 | 34.0145 | 72 |  |  | 2.0199 | 74 | 0 | 1.6423 | 168 | 94 | 1.8482 | 83 | 9 | 2.2392 | 53 | 21
297 | CTL1 | NE | Crestline | CTL1 | EOC |  |  |  | 4.1521 | 2 | 75 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 0 | 2 | 0 | 1 | 2 |  |  | 0.083042 | 202 | 48.1686 | 41 |  |  | 2 | 75 | 0 | 1.5628 | 186 | 111 | 1.7389 | 124 | 49 | 2.3003 | 37 | 38
306 | PE1 | NE | Pine Hills | PE1 | EOC |  |  |  | 6.8367 | 1.9999 | 76 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | 0.13673 | 170 | 29.2537 | 89 |  |  | 1.9999 | 76 | 0 | 1.604 | 177 | 101 | 1.7235 | 131 | 55 | 2.3018 | 35 | 41
142 | 352 | NE | Lilac | 352 | EOC |  |  |  | 11.4432 | 1.9999 | 77 | 3 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 0 | 1 | 2 |  |  | 0.22886 | 118 | 17.4777 | 153 |  |  | 1.9999 | 77 | 0 | 1.946 | 71 | 6 | 1.8382 | 87 | 10 | 2.1337 | 81 | 4
258 | 972 | NE | Creelman | 972-4 | EOC |  |  |  | 14.9597 | 1.9999 | 78 | 3 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.29919 | 78 | 13.3693 | 196 |  |  | 1.9999 | 78 | 0 | 1.9047 | 84 | 6 | 1.8535 | 81 | 3 | 2.1321 | 82 | 4
295 | 1458 | EA | Alpine | 1458 | 1458-22 | EOC |  |  | 8.5532 | 1.9899 | 79 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 3 |  |  | 0.17021 | 150 | 23.2661 | 117 |  |  | 1.9899 | 79 | 0 | 1.7687 | 134 | 55 | 1.8652 | 79 | 0 | 2.1364 | 79 | 0
64 | 214 | NE | Rincon | 214-538 | 214-15 | 214-16 |  |  | 9.3754 | 1.9899 | 80 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 3 | 3 | 1 | 3 | 1 | 2 |  |  | 0.18657 | 138 | 21.2258 | 122 |  |  | 1.9899 | 80 | 0 | 1.9336 | 76 | 4 | 1.8037 | 98 | 18 | 2.1426 | 76 | 4
184 | 449 | EA | Cameron | 449 | 449-1 | 449-13R |  |  | 11.3814 | 1.9899 | 81 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 1 | 2 |  |  | 0.22649 | 119 | 17.4846 | 152 |  |  | 1.9899 | 81 | 0 | 1.7007 | 152 | 71 | 1.7694 | 110 | 29 | 2.2243 | 55 | 26
75 | 221 | NE | Santa Ysabel | 221 | 221-33R |  |  |  | 4.5674 | 1.98 | 82 | 3 | 3 | 1 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.090435 | 198 | 43.3505 | 56 |  |  | 1.98 | 82 | 0 | 1.679 | 155 | 73 | 1.7586 | 118 | 36 | 2.2179 | 58 | 24
314 | SL1 | NE | Salton | SL1 | EOC |  |  |  | 4.8994 | 1.98 | 83 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | 0.097009 | 193 | 40.4128 | 63 |  |  | 1.98 | 83 | 0 | 1.5605 | 187 | 104 | 1.7018 | 140 | 57 | 2.2888 | 40 | 43
164 | 441 | EA | Glencliff | 441 | 441-27R | 441-30R |  |  | 10.8778 | 1.9799 | 84 | 3 | 2 | 1 | 3 | 3 | 1 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.21538 | 125 | 18.2021 | 145 |  |  | 1.9799 | 84 | 0 | 1.8706 | 91 | 7 | 1.8082 | 96 | 12 | 2.1345 | 80 | 4
14 | 79 | EA | Descanso | 79-676R | 79-658R | EOC |  |  | 15.6057 | 1.9798 | 85 | 3 | 3 | 2 | 2 | 2 | 0 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 0.30899 | 72 | 12.6877 | 203 |  |  | 1.9798 | 85 | 0 | 1.953 | 69 | 16 | 1.7773 | 106 | 21 | 2.1376 | 78 | 7
100 | 239 | NE | Pala | 239 | 239-15R | EOC | EOC |  | 22.1875 | 1.9798 | 86 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 1 |  |  | 0.43931 | 38 | 8.9239 | 245 |  |  | 1.9798 | 86 | 0 | 2.0209 | 50 | 36 | 1.8731 | 76 | 10 | 2.0496 | 108 | 22
71 | 217 | NE | Rincon | 217-835R | EOC |  |  |  | 26.3307 | 1.9797 | 87 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.52135 | 30 | 7.5197 | 257 |  |  | 1.9797 | 87 | 0 | 2.0208 | 51 | 36 | 1.8731 | 77 | 10 | 2.0495 | 109 | 22
105 | 240 | EA | Los Coches | 240-1095R | EOC |  |  |  | 9.6335 | 1.9699 | 88 | 3 | 1 | 2 | 3 | 3 | 0 | 1 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 2 | 2 |  |  | 0.18978 | 137 | 20.4494 | 127 |  |  | 1.9699 | 88 | 0 | 1.7984 | 118 | 30 | 1.8364 | 88 | 0 | 2.111 | 85 | 3
273 | 1021 | NE | Lilac | 1021-48 | EOC |  |  |  | 12.9259 | 1.9699 | 89 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 1 | 2 |  |  | 0.25464 | 99 | 15.2407 | 168 |  |  | 1.9699 | 89 | 0 | 1.8344 | 102 | 13 | 1.9239 | 63 | 26 | 2.0369 | 114 | 25
193 | 470 | NE | Felicita | 470-18R | EOC |  |  |  | 23.211 | 1.9698 | 90 | 1 | 1 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 0 | 3 | 3 | 3 | 1 | 3 | 3 |  |  | 0.45726 | 36 | 8.4874 | 251 |  |  | 1.9698 | 90 | 0 | 1.9981 | 60 | 30 | 2.0445 | 24 | 66 | 1.9072 | 147 | 57
296 | 1458 | EA | Alpine | 1458-22 | EOC |  |  |  | 9.3439 | 1.9599 | 91 | 3 | 2 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.18314 | 140 | 20.9762 | 125 |  |  | 1.9599 | 91 | 0 | 1.8271 | 105 | 14 | 1.7864 | 102 | 11 | 2.1215 | 83 | 8
141 | 351 | NE | Lilac | 351-819R | EOC |  |  |  | 10.5955 | 1.9599 | 92 | 1 | 2 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 2 | 1 |  |  | 0.20767 | 131 | 18.4985 | 140 |  |  | 1.9599 | 92 | 0 | 1.9085 | 83 | 9 | 1.9379 | 58 | 34 | 1.9887 | 130 | 38
68 | 215 | NE | Rincon | P216869 | EOC |  |  |  | 15.0229 | 1.9598 | 93 | 3 | 3 | 2 | 2 | 2 | 0 | 2 | 0 | 1 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.29445 | 79 | 13.0467 | 200 |  |  | 1.9598 | 93 | 0 | 1.8271 | 106 | 13 | 1.7864 | 103 | 10 | 2.1214 | 84 | 9
138 | 350 | NE | Lilac | 350-46R | EOC |  |  |  | 20.2322 | 1.9598 | 94 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 0.39655 | 48 | 9.6875 | 239 |  |  | 1.9598 | 94 | 0 | 2.0732 | 37 | 57 | 1.8762 | 75 | 19 | 1.9949 | 125 | 31
54 | 211 | NE | Warners | 211-280R | EOC |  |  |  | 13.5968 | 1.9499 | 95 | 1 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 2 | 1 | 1 | 3 | 3 | 1 | 1 | 1 | 3 |  |  | 0.26514 | 97 | 14.3416 | 181 |  |  | 1.9499 | 95 | 0 | 1.792 | 123 | 28 | 1.7199 | 132 | 37 | 2.1597 | 75 | 20
285 | 1138 | EA | Santee | 1138-6R | EOC |  |  |  | 13.9085 | 1.9499 | 96 | 3 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.27122 | 95 | 14.0202 | 186 |  |  | 1.9499 | 96 | 0 | 1.8373 | 101 | 5 | 1.7838 | 104 | 8 | 2.101 | 91 | 5
256 | 972 | NE | Creelman | 972-7 | P13262 |  |  |  | 15.3739 | 1.9498 | 97 | 3 | 2 | 3 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.29979 | 76 | 12.6839 | 204 |  |  | 1.9498 | 97 | 0 | 1.796 | 121 | 24 | 1.7992 | 100 | 3 | 2.0995 | 92 | 5
136 | 350 | NE | Lilac | 350-684R | EOC |  |  |  | 33.1557 | 1.9497 | 98 | 1 | 2 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 0.64654 | 21 | 5.8813 | 275 |  |  | 1.9497 | 98 | 0 | 2.0514 | 43 | 55 | 1.8652 | 80 | 18 | 1.9882 | 131 | 33
316 | TM1 | NE | Temecula (SCE) | TM1 | EOC |  |  |  | 2.9864 | 1.94 | 99 | 3 | 2 | 1 | 3 | 3 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 0 | 1 | 2 |  |  | 0.057935 | 228 | 64.9619 | 27 |  |  | 1.94 | 99 | 0 | 1.7837 | 125 | 26 | 1.7648 | 114 | 15 | 2.1085 | 87 | 12
252 | 971 | NE | Creelman | 971-26R | 971-24 |  |  |  | 9.2403 | 1.9399 | 100 | 3 | 2 | 2 | 3 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.17926 | 143 | 20.9949 | 124 |  |  | 1.9399 | 100 | 0 | 1.7836 | 126 | 26 | 1.7647 | 115 | 15 | 2.1084 | 88 | 12
150 | 356 | EA | Alpine | 356-19R | EOC |  |  |  | 14.9436 | 1.9399 | 101 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 3 | 1 | 1 | 2 |  |  | 0.28991 | 81 | 12.9822 | 202 |  |  | 1.9399 | 101 | 0 | 1.7691 | 133 | 32 | 1.8913 | 73 | 28 | 2.0173 | 121 | 20
242 | 908 | NE | Valley Center | 908 | 908-23 |  |  |  | 41.2864 | 1.9396 | 102 | 3 | 2 | 3 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.80096 | 10 | 4.6989 | 284 |  |  | 1.9396 | 102 | 0 | 2.1254 | 26 | 76 | 1.8791 | 74 | 28 | 1.94 | 141 | 39
52 | 210 | NE | Warners | P227546 | EOC |  |  |  | 10.2898 | 1.9299 | 103 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 2 | 2 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.19859 | 134 | 18.7565 | 138 |  |  | 1.9299 | 103 | 0 | 1.8258 | 107 | 4 | 1.7704 | 109 | 6 | 2.0742 | 98 | 5
24 | 175 | NE | Poway | 175-24R | 175-90R |  |  |  | 14.2606 | 1.9299 | 104 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 3 | 3 |  |  | 0.27523 | 93 | 13.5338 | 193 |  |  | 1.9299 | 104 | 0 | 1.9803 | 65 | 39 | 1.9147 | 66 | 38 | 1.9291 | 142 | 38
178 | 445 | EA | Boulevard | 445-24R | EOC |  |  |  | 22.6352 | 1.9298 | 105 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 0 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.43686 | 40 | 8.5265 | 250 |  |  | 1.9298 | 105 | 0 | 1.7618 | 136 | 31 | 1.7537 | 119 | 14 | 2.1018 | 90 | 15
56 | 212 | NE | Warners | 212 | P19585 | 212-632R | 212-630R |  | 23.6792 | 1.9298 | 106 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 3 | 3 | 2 | 0 | 3 | 3 | 1 | 0 | 2 | 2 |  |  | 0.45701 | 37 | 8.1506 | 253 |  |  | 1.9298 | 106 | 0 | 1.9493 | 70 | 36 | 1.7241 | 130 | 24 | 2.0787 | 97 | 9
72 | 220 | NE | Santa Ysabel | 220 | 220-294R |  |  |  | 7.4 | 1.9199 | 107 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 2 | 2 | 0 | 2 | 1 |  |  | 0.14208 | 166 | 25.9459 | 101 |  |  | 1.9199 | 107 | 0 | 1.7402 | 145 | 38 | 1.743 | 121 | 14 | 2.0954 | 94 | 13
10 | 78 | EA | Descanso | 78 | EOC |  |  |  | 12.1587 | 1.9099 | 108 | 3 | 3 | 1 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 3 | 3 |  |  | 0.23223 | 114 | 15.7089 | 162 |  |  | 1.9099 | 108 | 0 | 1.7544 | 140 | 32 | 1.8196 | 92 | 16 | 2.0148 | 122 | 14
173 | 445 | EA | Boulevard | 445 | 445-23R | 445-17R | 445-19R | 445-21R | 11.1438 | 1.8999 | 109 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 3 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.21173 | 128 | 17.0499 | 156 |  |  | 1.8999 | 109 | 0 | 1.8203 | 111 | 2 | 1.675 | 151 | 42 | 2.087 | 95 | 14
135 | 350 | NE | Lilac | 350 | 350-15R | 350-684R | 350-33R |  | 14.4254 | 1.8999 | 110 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.27408 | 94 | 13.1712 | 199 |  |  | 1.8999 | 110 | 0 | 1.8883 | 87 | 23 | 1.7708 | 108 | 2 | 1.999 | 124 | 14
272 | 1021 | NE | Lilac | 1021 | 1021-48 |  |  |  | 16.2631 | 1.8998 | 111 | 3 | 1 | 2 | 3 | 2 | 0 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 1 | 1 |  |  | 0.309 | 71 | 11.6829 | 215 |  |  | 1.8998 | 111 | 0 | 1.7234 | 148 | 37 | 1.8324 | 89 | 22 | 1.9927 | 128 | 17
200 | 520 | NE | Avocado | 520 | 520-18R | 520-26AE |  |  | 18.6953 | 1.8998 | 112 | 1 | 2 | 2 | 2 | 3 | 0 | 3 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.35521 | 57 | 10.163 | 233 |  |  | 1.8998 | 112 | 0 | 1.9428 | 72 | 40 | 1.811 | 95 | 17 | 1.9558 | 136 | 24
51 | 210 | NE | Warners | 210-9R | P227546 | EOC |  |  | 4.0625 | 1.89 | 113 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 3 |  |  | 0.076781 | 208 | 46.5231 | 50 |  |  | 1.89 | 113 | 0 | 1.7801 | 128 | 15 | 1.7116 | 137 | 24 | 2.0497 | 107 | 6
205 | 520 | NE | Avocado | 520-18R | 520-33R |  |  |  | 7.3201 | 1.8899 | 114 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.13835 | 168 | 25.8194 | 103 |  |  | 1.8899 | 114 | 0 | 1.8254 | 108 | 6 | 1.7754 | 107 | 7 | 1.991 | 129 | 15
207 | 520 | NE | Avocado | 520-1053 | EOC |  |  |  | 17.4259 | 1.8898 | 115 | 1 | 2 | 2 | 2 | 3 | 0 | 1 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 2 |  |  | 0.32935 | 64 | 10.8459 | 226 |  |  | 1.8898 | 115 | 0 | 1.8799 | 90 | 25 | 1.8155 | 94 | 21 | 1.9477 | 137 | 22
174 | 445 | EA | Boulevard | 445-17R | EOC |  |  |  | 21.1485 | 1.8898 | 116 | 3 | 3 | 1 | 2 | 3 | 0 | 2 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.39971 | 47 | 8.9368 | 244 |  |  | 1.8898 | 116 | 0 | 1.7985 | 117 | 1 | 1.6641 | 157 | 41 | 2.0804 | 96 | 20
61 | 212 | NE | Warners | 212-652R | EOC |  |  |  | 28.8727 | 1.8897 | 117 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 0 | 2 | 2 | 2 | 3 | 3 | 1 | 0 | 2 | 2 |  |  | 0.54569 | 27 | 6.546 | 268 |  |  | 1.8897 | 117 | 0 | 1.8623 | 93 | 24 | 1.6805 | 149 | 32 | 2.0526 | 106 | 11
177 | 445 | EA | Boulevard | 445-23R | 445-24R | EOC |  |  | 1.2598 | 1.88 | 118 | 3 | 3 | 1 | 2 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.023685 | 260 | 149.2243 | 9 |  |  | 1.88 | 118 | 0 | 1.6533 | 163 | 45 | 1.6996 | 142 | 24 | 2.0694 | 100 | 18
261 | 974 | NE | Creelman | 974 | 974-7 |  |  |  | 6.3195 | 1.8799 | 119 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 3 | 3 |  |  | 0.11881 | 182 | 29.7492 | 86 |  |  | 1.8799 | 119 | 0 | 1.4884 | 203 | 84 | 1.7611 | 116 | 3 | 2.0631 | 101 | 18
175 | 445 | EA | Boulevard | 445-19R | EOC |  |  |  | 12.8462 | 1.8799 | 120 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.24151 | 109 | 14.6347 | 178 |  |  | 1.8799 | 120 | 0 | 1.7768 | 131 | 11 | 1.6533 | 162 | 42 | 2.074 | 99 | 21
139 | 350 | NE | Lilac | 350-33R | EOC |  |  |  | 15.0167 | 1.8798 | 121 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.28231 | 86 | 12.5194 | 206 |  |  | 1.8798 | 121 | 0 | 1.8448 | 97 | 24 | 1.7491 | 120 | 1 | 1.986 | 132 | 11
114 | 249 | NE | Pala | 249 | EOC |  |  |  | 15.0523 | 1.8798 | 122 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 0 | 3 | 2 | 2 | 0 | 3 | 3 |  |  | 0.28298 | 84 | 12.4898 | 207 |  |  | 1.8798 | 122 | 0 | 1.9128 | 81 | 41 | 1.8449 | 85 | 37 | 1.898 | 148 | 26
287 | 1166 | EA | Loveland | 1166 | 1166-18R | EOC |  |  | 4.3964 | 1.87 | 123 | 3 | 2 | 1 | 3 | 3 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 2 | 1 |  |  | 0.082213 | 203 | 42.5348 | 59 |  |  | 1.87 | 123 | 0 | 1.6315 | 170 | 47 | 1.6887 | 147 | 24 | 2.0628 | 102 | 21
15 | 79 | EA | Descanso | 79-658R | 79-660R |  |  |  | 13.2152 | 1.8699 | 124 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.24712 | 103 | 14.1504 | 184 |  |  | 1.8699 | 124 | 0 | 1.7911 | 124 | 0 | 1.73 | 128 | 4 | 1.9934 | 127 | 3
53 | 211 | NE | Warners | 211 | 211-280R | 211-262R |  |  | 15.0354 | 1.8698 | 125 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 0.28116 | 87 | 12.4373 | 210 |  |  | 1.8698 | 125 | 0 | 1.7777 | 130 | 5 | 1.6743 | 152 | 27 | 2.0381 | 113 | 12
303 | MAN1 | NE | Manzanita | MAN1 | EOC |  |  |  | 3.9542 | 1.86 | 126 | 3 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 0.073548 | 212 | 47.039 | 48 |  |  | 1.86 | 126 | 0 | 1.4594 | 209 | 83 | 1.6127 | 175 | 49 | 2.1412 | 77 | 49
274 | 1022 | NE | Lilac | 1022-15 | EOC |  |  |  | 7.8924 | 1.8599 | 127 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 0 | 3 | 2 | 1 | 1 |  |  | 0.1468 | 160 | 23.5669 | 114 |  |  | 1.8599 | 127 | 0 | 1.5953 | 179 | 52 | 1.8044 | 97 | 30 | 1.9652 | 135 | 8
259 | 973 | NE | Creelman | 973 | 973-27 | EOC |  |  | 12.5491 | 1.8599 | 128 | 3 | 2 | 1 | 1 | 3 | 1 | 2 | 3 | 0 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 0.23341 | 113 | 14.8218 | 174 |  |  | 1.8599 | 128 | 0 | 1.8281 | 104 | 24 | 1.8386 | 86 | 42 | 1.8834 | 149 | 21
176 | 445 | EA | Boulevard | 445-21R | EOC |  |  |  | 25.8837 | 1.8597 | 129 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.48144 | 34 | 7.186 | 260 |  |  | 1.8597 | 129 | 0 | 1.7332 | 146 | 17 | 1.6314 | 168 | 39 | 2.0608 | 103 | 26
170 | 444 | EA | Boulevard | 444 | P41993 |  |  |  | 6.5136 | 1.8499 | 130 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 1 | 1 | 1 | 3 |  |  | 0.1205 | 180 | 28.402 | 90 |  |  | 1.8499 | 130 | 0 | 1.6704 | 161 | 31 | 1.6361 | 166 | 36 | 2.0529 | 105 | 25
16 | 79 | EA | Descanso | 79-660R | 79-19R |  |  |  | 7.7002 | 1.8499 | 131 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.14245 | 165 | 24.0254 | 112 |  |  | 1.8499 | 131 | 0 | 1.7477 | 144 | 13 | 1.7083 | 138 | 7 | 1.9804 | 133 | 2
104 | 240 | EA | Los Coches | 240-1097R | EOC |  |  |  | 12.7585 | 1.8499 | 132 | 3 | 1 | 1 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.23603 | 112 | 14.5001 | 180 |  |  | 1.8499 | 132 | 0 | 1.7796 | 129 | 3 | 1.7165 | 135 | 3 | 1.9664 | 134 | 2
60 | 212 | NE | Warners | 212-650R | EOC |  |  |  | 21.3939 | 1.8498 | 133 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 3 | 3 | 3 | 1 | 0 | 2 | 1 |  |  | 0.39579 | 49 | 8.6473 | 248 |  |  | 1.8498 | 133 | 0 | 1.8166 | 112 | 21 | 1.6217 | 170 | 37 | 2.0281 | 118 | 15
172 | 444 | EA | Boulevard | P42077 | EOC |  |  |  | 23.6938 | 1.8498 | 134 | 1 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 0 | 2 | 3 | 1 | 1 | 2 | 3 |  |  | 0.43833 | 39 | 7.808 | 255 |  |  | 1.8498 | 134 | 0 | 1.8846 | 89 | 45 | 1.7176 | 133 | 1 | 1.9401 | 140 | 6
22 | 157 | EA | Barrett | 157-67R | 157-87R | 157-75R | 157-77R |  | 2.1 | 1.84 | 135 | 3 | 3 | 0 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 3 | 1 |  |  | 0.03864 | 244 | 87.619 | 18 |  |  | 1.84 | 135 | 0 | 1.9949 | 62 | 73 | 1.8193 | 93 | 42 | 1.8181 | 158 | 23
275 | 1030 | NE | Valley Center | 1030 | 1030-14 |  |  |  | 4.7856 | 1.84 | 136 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 3 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.088055 | 199 | 38.4486 | 65 |  |  | 1.84 | 136 | 0 | 1.5663 | 185 | 49 | 1.656 | 160 | 24 | 2.0433 | 111 | 25
166 | 441 | EA | Glencliff | 441-30R | EOC |  |  |  | 6.1053 | 1.8399 | 137 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.11234 | 185 | 30.1377 | 85 |  |  | 1.8399 | 137 | 0 | 1.6899 | 154 | 17 | 1.6099 | 178 | 41 | 2.048 | 110 | 27
211 | 521 | NE | Avocado | 521-32R | EOC |  |  |  | 9.1759 | 1.8399 | 138 | 3 | 2 | 2 | 1 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 0.16884 | 151 | 20.0524 | 131 |  |  | 1.8399 | 138 | 0 | 1.7486 | 143 | 5 | 1.7293 | 129 | 9 | 1.9445 | 139 | 1
58 | 212 | NE | Warners | 212-632R | 212-650R | 212-652R |  |  | 11.8131 | 1.8399 | 139 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 0 | 2 | 2 | 1 | 3 | 3 | 1 | 0 | 1 | 2 |  |  | 0.21736 | 124 | 15.576 | 164 |  |  | 1.8399 | 139 | 0 | 1.795 | 122 | 17 | 1.611 | 177 | 38 | 2.0217 | 120 | 19
145 | 354 | NE | Lilac | 354 | 354-5 |  |  |  | 17.6538 | 1.8398 | 140 | 1 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.32483 | 66 | 10.4227 | 230 |  |  | 1.8398 | 140 | 0 | 1.8536 | 95 | 45 | 1.7304 | 127 | 13 | 1.9182 | 146 | 6
171 | 444 | EA | Boulevard | P41993 | P42077 |  |  |  | 7.8121 | 1.8299 | 141 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 1 | 1 | 1 | 3 |  |  | 0.14296 | 163 | 23.4251 | 115 |  |  | 1.8299 | 141 | 0 | 1.627 | 171 | 30 | 1.6144 | 174 | 33 | 2.0398 | 112 | 29
1 | 67 | EA | Barrett | 67 | 67-24R |  |  |  | 35.8356 | 1.8296 | 142 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 2 |  |  | 0.65579 | 19 | 5.1067 | 280 |  |  | 1.8296 | 142 | 0 | 1.8863 | 88 | 54 | 1.7596 | 117 | 25 | 1.8683 | 151 | 9
65 | 214 | NE | Rincon | 214-15 | EOC |  |  |  | 3.8729 | 1.82 | 143 | 3 | 2 | 1 | 2 | 3 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 3 | 3 | 2 |  |  | 0.070487 | 215 | 46.993 | 49 |  |  | 1.82 | 143 | 0 | 1.6732 | 160 | 17 | 1.6994 | 143 | 0 | 1.9454 | 138 | 5
50 | 210 | NE | Warners | 210 | 210-9R |  |  |  | 6.1955 | 1.8199 | 144 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 1 |  |  | 0.11276 | 184 | 29.3764 | 87 |  |  | 1.8199 | 144 | 0 | 1.7103 | 150 | 6 | 1.6047 | 181 | 37 | 2.0071 | 123 | 21
165 | 441 | EA | Glencliff | 441-27R | EOC |  |  |  | 6.7186 | 1.8199 | 145 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.12228 | 177 | 27.0891 | 94 |  |  | 1.8199 | 145 | 0 | 1.6464 | 166 | 21 | 1.5881 | 185 | 40 | 2.0349 | 115 | 30
231 | 597 | NE | San Marcos | 597-636 | EOC |  |  |  | 12.7426 | 1.8199 | 146 | 1 | 1 | 3 | 2 | 2 | 0 | 3 | 1 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 2 | 2 |  |  | 0.23192 | 115 | 14.2828 | 182 |  |  | 1.8199 | 146 | 0 | 1.7545 | 139 | 7 | 1.8507 | 82 | 64 | 1.8126 | 161 | 15
87 | 230 | NE | Monserate | 230-133 | EOC |  |  |  | 17.6042 | 1.8198 | 147 | 3 | 1 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.3204 | 68 | 10.3385 | 231 |  |  | 1.8198 | 147 | 0 | 1.9379 | 74 | 73 | 1.7418 | 123 | 24 | 1.8497 | 155 | 8
311 | RB1 | NE | Rainbow 1 | RB1-19R | EOC |  |  |  | 5.9968 | 1.8099 | 148 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 0 | 2 | 2 | 1 | 1 |  |  | 0.10854 | 188 | 30.1829 | 84 |  |  | 1.8099 | 148 | 0 | 1.4598 | 208 | 60 | 1.6388 | 165 | 17 | 2.0221 | 119 | 29
69 | 216 | NE | Rincon | 216 | EOC |  |  |  | 6.6792 | 1.8099 | 149 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 0 | 3 | 3 |  |  | 0.12089 | 178 | 27.0992 | 93 |  |  | 1.8099 | 149 | 0 | 1.7607 | 137 | 12 | 1.7689 | 111 | 38 | 1.8524 | 154 | 5
59 | 212 | NE | Warners | 212-630R | EOC |  |  |  | 3.6169 | 1.8 | 150 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 3 | 1 | 0 | 3 | 1 |  |  | 0.065103 | 219 | 49.767 | 36 |  |  | 1.8 | 150 | 0 | 1.6669 | 162 | 12 | 1.583 | 187 | 37 | 1.9941 | 126 | 24
213 | 521 | NE | Avocado | 521-14R | EOC |  |  |  | 11.8812 | 1.7999 | 151 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 2 | 2 | 1 | 2 | 3 | 2 | 1 | 2 | 2 |  |  | 0.21386 | 127 | 15.1499 | 170 |  |  | 1.7999 | 151 | 0 | 1.7801 | 127 | 24 | 1.7426 | 122 | 29 | 1.8474 | 156 | 5
91 | 233 | NE | Monserate | 233-49 | EOC |  |  |  | 24.2447 | 1.7998 | 152 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 0.4364 | 41 | 7.4243 | 259 |  |  | 1.7998 | 152 | 0 | 2.0262 | 49 | 103 | 1.8324 | 90 | 62 | 1.7208 | 176 | 24
302 | JU1 | NE | Julian | JU1 | EOC |  |  |  | 2.5316 | 1.79 | 153 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 |  |  | 0.045316 | 237 | 70.7055 | 25 |  |  | 1.79 | 153 | 0 | 1.3072 | 232 | 79 | 1.5367 | 205 | 52 | 2.0955 | 93 | 60
204 | 520 | NE | Avocado | 520-1054 | 520-13 |  |  |  | 5.1127 | 1.7899 | 154 | 3 | 2 | 1 | 2 | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 0.091517 | 196 | 35.0109 | 69 |  |  | 1.7899 | 154 | 0 | 1.608 | 176 | 22 | 1.6668 | 155 | 1 | 1.9258 | 145 | 9
67 | 215 | NE | Rincon | 215 | P216869 |  |  |  | 8.8807 | 1.7899 | 155 | 3 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.15896 | 158 | 20.1561 | 130 |  |  | 1.7899 | 155 | 0 | 1.8089 | 113 | 42 | 1.6927 | 146 | 9 | 1.8579 | 152 | 3
92 | 233 | NE | Monserate | 233-14 | EOC |  |  |  | 22.4464 | 1.7898 | 156 | 1 | 1 | 3 | 1 | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 3 |  |  | 0.40179 | 45 | 7.9746 | 254 |  |  | 1.7898 | 156 | 0 | 2.0045 | 57 | 99 | 1.8215 | 91 | 65 | 1.7143 | 178 | 22
137 | 350 | NE | Lilac | 350-15R | 350-46R |  |  |  | 29.4682 | 1.7897 | 157 | 1 | 2 | 2 | 2 | 2 | 0 | 3 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 0.52748 | 29 | 6.0743 | 272 |  |  | 1.7897 | 157 | 0 | 1.9045 | 85 | 72 | 1.7173 | 134 | 23 | 1.8161 | 160 | 3
93 | 234 | NE | Monserate | 234 | EOC |  |  |  | 17.8201 | 1.7798 | 158 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.3172 | 69 | 9.9887 | 236 |  |  | 1.7798 | 158 | 0 | 1.9148 | 80 | 78 | 1.7149 | 136 | 22 | 1.7958 | 164 | 6
161 | 411 | EA | Granite | 411-8 | EOC |  |  |  | 7.1159 | 1.7699 | 159 | 1 | 1 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.12595 | 176 | 24.8738 | 106 |  |  | 1.7699 | 159 | 0 | 1.7283 | 147 | 12 | 1.7657 | 113 | 46 | 1.7831 | 169 | 10
208 | 521 | NE | Avocado | 521 | 521-27R | 521-18R |  |  | 14.1765 | 1.7699 | 160 | 3 | 2 | 3 | 1 | 1 | 0 | 3 | 3 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.25092 | 101 | 12.4854 | 208 |  |  | 1.7699 | 160 | 0 | 1.7973 | 120 | 40 | 1.6792 | 150 | 10 | 1.831 | 157 | 3
84 | 230 | NE | Monserate | 230-4R | 230-11 | EOC |  |  | 24.6432 | 1.7698 | 161 | 3 | 1 | 3 | 1 | 2 | 2 | 3 | 1 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.43618 | 42 | 7.1825 | 261 |  |  | 1.7698 | 161 | 0 | 1.8291 | 103 | 58 | 1.6874 | 148 | 13 | 1.817 | 159 | 2
11 | 79 | EA | Descanso | 79 | 79-676R | 79-673R |  |  | 6.5 | 1.7599 | 162 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.1144 | 183 | 27.0769 | 95 |  |  | 1.7599 | 162 | 0 | 1.6757 | 157 | 5 | 1.5643 | 195 | 33 | 1.9264 | 144 | 18
17 | 79 | EA | Descanso | 79-19R | EOC |  |  |  | 9.0712 | 1.7599 | 163 | 3 | 3 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 1 |  |  | 0.15965 | 156 | 19.402 | 133 |  |  | 1.7599 | 163 | 0 | 1.7169 | 149 | 14 | 1.5489 | 201 | 38 | 1.9279 | 143 | 20
102 | 239 | NE | Pala | EOC | EOC |  |  |  | 11.9314 | 1.7599 | 164 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 2 | 1 |  |  | 0.20999 | 129 | 14.7509 | 175 |  |  | 1.7599 | 164 | 0 | 1.7982 | 119 | 45 | 1.7003 | 141 | 23 | 1.7951 | 165 | 1
8 | 75 | EA | Jamacha | 75-32R | P171361 |  |  |  | 16.2623 | 1.7598 | 165 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 1 | 2 | 2 | 0 | 3 | 3 | 2 | 3 | 1 | 2 |  |  | 0.28622 | 83 | 10.8226 | 227 |  |  | 1.7598 | 165 | 0 | 1.9393 | 73 | 92 | 1.789 | 101 | 64 | 1.6948 | 179 | 14
88 | 231 | NE | Monserate | 231 | Z317920 |  |  |  | 32.7089 | 1.7397 | 166 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.56913 | 25 | 5.3197 | 279 |  |  | 1.7397 | 166 | 0 | 1.9781 | 66 | 100 | 1.7363 | 126 | 40 | 1.6847 | 182 | 16
147 | 354 | NE | Lilac | 354-24AE | EOC |  |  |  | 3.5104 | 1.71 | 167 | 1 | 2 | 1 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 0.060028 | 224 | 48.7122 | 40 |  |  | 1.71 | 167 | 0 | 1.6484 | 165 | 2 | 1.6614 | 158 | 9 | 1.7611 | 171 | 4
310 | RB1 | NE | Rainbow 1 | RB1 | RB1-19R |  |  |  | 9.328 | 1.7099 | 168 | 3 | 2 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 1 | 1 |  |  | 0.15951 | 157 | 18.3318 | 142 |  |  | 1.7099 | 168 | 0 | 1.4341 | 217 | 49 | 1.5798 | 188 | 20 | 1.8736 | 150 | 18
260 | 973 | NE | Creelman | 973-626R | EOC |  |  |  | 10.7032 | 1.6999 | 169 | 3 | 2 | 1 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 3 | 2 | 2 | 1 | 1 | 1 |  |  | 0.18195 | 141 | 15.8831 | 159 |  |  | 1.6999 | 169 | 0 | 1.6452 | 167 | 2 | 1.6031 | 183 | 14 | 1.7854 | 168 | 1
117 | 283 | EA | Loveland | 283 | 283-29 |  |  |  | 5.4028 | 1.6899 | 170 | 3 | 2 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.091308 | 197 | 31.2798 | 78 |  |  | 1.6899 | 170 | 0 | 1.5915 | 180 | 10 | 1.584 | 186 | 16 | 1.7928 | 166 | 4
209 | 521 | NE | Avocado | 521-18R | 521-5 |  |  |  | 11.3989 | 1.6899 | 171 | 3 | 3 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.19264 | 135 | 14.826 | 173 |  |  | 1.6899 | 171 | 0 | 1.7512 | 141 | 30 | 1.6254 | 169 | 2 | 1.7233 | 175 | 4
158 | 396 | EA | Santee | P970961 | EOC |  |  |  | 12.3117 | 1.6899 | 172 | 1 | 1 | 3 | 2 | 3 | 0 | 2 | 1 | 2 | 2 | 0 | 1 | 3 | 2 | 0 | 1 | 1 |  |  | 0.20807 | 130 | 13.7267 | 191 |  |  | 1.6899 | 172 | 0 | 1.6007 | 178 | 6 | 1.5603 | 196 | 24 | 1.8081 | 162 | 10
13 | 79 | EA | Descanso | Z371551 | P377371 | EOC |  |  | 2.1905 | 1.68 | 173 | 3 | 3 | 0 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.036801 | 247 | 76.6938 | 23 |  |  | 1.68 | 173 | 0 | 1.5379 | 192 | 19 | 1.5649 | 194 | 21 | 1.8002 | 163 | 10
298 | DV1 | EA | Dehesa Valley | DV1 | EOC |  |  |  | 5.9562 | 1.6799 | 174 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 0 | 1 | 2 | 0 | 2 | 0 | 2 | 1 | 2 | 1 |  |  | 0.10007 | 192 | 28.2057 | 92 |  |  | 1.6799 | 174 | 0 | 1.3689 | 226 | 52 | 1.5472 | 202 | 28 | 1.8541 | 153 | 21
212 | 521 | NE | Avocado | 521-27R | 521-14R |  |  |  | 19.5106 | 1.6798 | 175 | 1 | 3 | 2 | 1 | 1 | 1 | 3 | 2 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.32778 | 65 | 8.6107 | 249 |  |  | 1.6798 | 175 | 0 | 1.8252 | 109 | 66 | 1.6393 | 164 | 11 | 1.6751 | 184 | 9
113 | 248 | EA | Los Coches | 248 | EOC |  |  |  | 21.5934 | 1.6798 | 176 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 0.36277 | 55 | 7.7802 | 256 |  |  | 1.6798 | 176 | 0 | 1.8983 | 86 | 90 | 1.6321 | 167 | 9 | 1.6627 | 186 | 10
271 | 1001 | NC | Rancho Santa Fe | 1001-39 | EOC |  |  |  | 4.7752 | 1.67 | 177 | 1 | 1 | 3 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 1 |  |  | 0.079746 | 206 | 34.9724 | 70 |  |  | 1.67 | 177 | 0 | 1.4697 | 206 | 29 | 1.6724 | 154 | 23 | 1.7164 | 177 | 0
19 | 91 | EA | Jamacha | P370004 | EOC |  |  |  | 5.7009 | 1.6699 | 178 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | 1 |  |  | 0.095206 | 194 | 29.2934 | 88 |  |  | 1.6699 | 178 | 0 | 1.5295 | 195 | 17 | 1.6096 | 179 | 1 | 1.7488 | 173 | 5
245 | 909 | NE | Valley Center | 909-6 | EOC |  |  |  | 11.1458 | 1.6699 | 179 | 3 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 2 | 2 | 0 | 3 | 3 |  |  | 0.18614 | 139 | 14.9832 | 172 |  |  | 1.6699 | 179 | 0 | 1.616 | 174 | 5 | 1.6581 | 159 | 20 | 1.6917 | 181 | 2
233 | 599 | NE | San Marcos | 599-1181 | EOC |  |  |  | 6.2038 | 1.6599 | 180 | 1 | 1 | 1 | 3 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 2 | 2 | 3 | 1 | 1 | 2 |  |  | 0.10298 | 189 | 26.7578 | 97 |  |  | 1.6599 | 180 | 0 | 1.5757 | 184 | 4 | 1.6946 | 145 | 35 | 1.6543 | 188 | 8
143 | 353 | NE | Lilac | 353 | 353-914R |  |  |  | 6.7023 | 1.6599 | 181 | 1 | 2 | 1 | 2 | 3 | 0 | 2 | 2 | 0 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.11126 | 186 | 24.7677 | 107 |  |  | 1.6599 | 181 | 0 | 1.6221 | 172 | 9 | 1.5763 | 192 | 11 | 1.7315 | 174 | 7
2 | 67 | EA | Barrett | 67-24R | EOC |  |  |  | 12.1398 | 1.6599 | 182 | 3 | 2 | 2 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.20152 | 133 | 13.6741 | 192 |  |  | 1.6599 | 182 | 0 | 1.5582 | 189 | 7 | 1.5597 | 198 | 16 | 1.7592 | 172 | 10
6 | 75 | EA | Jamacha | 75-996R | 75-40 |  |  |  | 14.7434 | 1.6599 | 183 | 1 | 1 | 2 | 1 | 2 | 1 | 3 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 3 | 2 | 2 |  |  | 0.24474 | 104 | 11.2593 | 222 |  |  | 1.6599 | 183 | 0 | 1.8405 | 98 | 85 | 1.7371 | 125 | 58 | 1.5586 | 201 | 18
90 | 233 | NE | Monserate | 233 | 233-49 | 233-14 |  |  | 16.7288 | 1.6598 | 184 | 1 | 1 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 0.2777 | 92 | 9.923 | 238 |  |  | 1.6598 | 184 | 0 | 1.8044 | 115 | 69 | 1.6495 | 163 | 21 | 1.6327 | 193 | 9
157 | 387 | EA | Granite | Z272783 | EOC |  |  |  | 3.4345 | 1.65 | 185 | 1 | 2 | 0 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 1 | 2 | 2 |  |  | 0.056669 | 230 | 48.0424 | 42 |  |  | 1.65 | 185 | 0 | 1.5128 | 199 | 14 | 1.6992 | 144 | 41 | 1.6463 | 189 | 4
78 | 221 | NE | Santa Ysabel | P519130 | EOC |  |  |  | 14.7973 | 1.6499 | 186 | 3 | 3 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 0.24416 | 106 | 11.1506 | 223 |  |  | 1.6499 | 186 | 0 | 1.5818 | 183 | 3 | 1.6126 | 176 | 10 | 1.6941 | 180 | 6
125 | 307 | NC | Rancho Santa Fe | EOC | EOC |  |  |  | 3.7222 | 1.64 | 187 | 1 | 2 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 3 | 2 |  |  | 0.061043 | 222 | 44.0604 | 55 |  |  | 1.64 | 187 | 0 | 1.4499 | 213 | 26 | 1.7037 | 139 | 48 | 1.6382 | 191 | 4
247 | 920 | NE | Pomerado | P108024 | EOC |  |  |  | 4.9241 | 1.64 | 188 | 1 | 1 | 1 | 3 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 0.080754 | 205 | 33.3059 | 74 |  |  | 1.64 | 188 | 0 | 1.5323 | 193 | 5 | 1.6729 | 153 | 35 | 1.6413 | 190 | 2
307 | RA1 | NE | Ramona | RA1 | EOC |  |  |  | 10.767 | 1.6399 | 189 | 3 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.17658 | 144 | 15.2317 | 169 |  |  | 1.6399 | 189 | 0 | 1.6744 | 159 | 30 | 1.5793 | 189 | 0 | 1.6768 | 183 | 6
215 | 522 | NE | Avocado | 522-25 | EOC |  |  |  | 14.515 | 1.6399 | 190 | 1 | 2 | 3 | 1 | 1 | 1 | 3 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.23805 | 111 | 11.2987 | 221 |  |  | 1.6399 | 190 | 0 | 1.7702 | 132 | 58 | 1.6041 | 182 | 8 | 1.6351 | 192 | 2
12 | 79 | EA | Descanso | 79-673R | Z371551 |  |  |  | 10.3 | 1.6199 | 191 | 3 | 3 | 0 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 0.16686 | 153 | 15.7282 | 161 |  |  | 1.6199 | 191 | 0 | 1.531 | 194 | 3 | 1.4535 | 220 | 29 | 1.7656 | 170 | 21
26 | 176 | NE | Poway | 176 | 176-26R | 176-36R |  |  | 14.0405 | 1.6099 | 192 | 1 | 1 | 2 | 2 | 2 | 0 | 3 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.22605 | 121 | 11.4668 | 219 |  |  | 1.6099 | 192 | 0 | 1.705 | 151 | 41 | 1.5715 | 193 | 1 | 1.6156 | 195 | 3
244 | 909 | NE | Valley Center | 909 | 909-6 |  |  |  | 17.4189 | 1.6098 | 193 | 3 | 2 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 2 | 0 | 1 | 2 |  |  | 0.28044 | 89 | 9.2428 | 242 |  |  | 1.6098 | 193 | 0 | 1.6091 | 175 | 18 | 1.5466 | 203 | 10 | 1.6572 | 187 | 6
9 | 75 | EA | Jamacha | P171361 | EOC |  |  |  | 15.3894 | 1.5898 | 194 | 3 | 1 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 1 | 0 | 3 | 3 | 1 | 3 | 3 | 3 |  |  | 0.24469 | 105 | 10.3318 | 232 |  |  | 1.5898 | 194 | 0 | 1.6749 | 158 | 36 | 1.6054 | 180 | 14 | 1.5578 | 202 | 8
246 | 920 | NE | Pomerado | P137565 | EOC |  |  |  | 1.989 | 1.57 | 195 | 1 | 1 | 0 | 3 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 3 | 1 |  |  | 0.031228 | 251 | 78.9335 | 22 |  |  | 1.57 | 195 | 0 | 1.4986 | 202 | 7 | 1.6536 | 161 | 34 | 1.5247 | 207 | 12
304 | MOR1 | NE | Moore | MOR1 | EOC |  |  |  | 2.8384 | 1.57 | 196 | 3 | 2 | 2 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 0.044564 | 238 | 55.3119 | 33 |  |  | 1.57 | 196 | 0 | 1.2122 | 245 | 49 | 1.3969 | 236 | 40 | 1.7855 | 167 | 29
210 | 521 | NE | Avocado | 521-5 | 521-32R |  |  |  | 10.7176 | 1.5699 | 197 | 3 | 2 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 0.16827 | 152 | 14.6488 | 177 |  |  | 1.5699 | 197 | 0 | 1.6407 | 169 | 28 | 1.56 | 197 | 0 | 1.5602 | 200 | 3
110 | 246 | EA | Los Coches | 246-9 | 246-11 |  |  |  | 11.429 | 1.5699 | 198 | 1 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 1 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 3 |  |  | 0.17943 | 142 | 13.737 | 190 |  |  | 1.5699 | 198 | 0 | 1.8458 | 96 | 102 | 1.6653 | 156 | 42 | 1.4322 | 224 | 26
218 | 524 | EA | Jamacha | 524-30 | 524-13 |  |  |  | 3.272 | 1.56 | 199 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.051043 | 234 | 47.6777 | 45 |  |  | 1.56 | 199 | 0 | 1.5912 | 181 | 18 | 1.6202 | 171 | 28 | 1.5074 | 210 | 11
194 | 470 | NE | Felicita | 470-30 | EOC |  |  |  | 5.5282 | 1.5599 | 200 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 0.08624 | 200 | 28.2188 | 91 |  |  | 1.5599 | 200 | 0 | 1.5912 | 182 | 18 | 1.6202 | 172 | 28 | 1.5074 | 211 | 11
187 | 450 | NE | Ash | 450-18 | EOC |  |  |  | 8.5977 | 1.5599 | 201 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 3 | 1 | 1 | 1 | 2 |  |  | 0.13412 | 171 | 18.1443 | 147 |  |  | 1.5599 | 201 | 0 | 1.5284 | 196 | 5 | 1.4214 | 230 | 29 | 1.671 | 185 | 16
28 | 176 | NE | Poway | 176-36R | EOC |  |  |  | 8.5275 | 1.5499 | 202 | 3 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.13218 | 172 | 18.1766 | 146 |  |  | 1.5499 | 202 | 0 | 1.4788 | 204 | 2 | 1.4815 | 214 | 12 | 1.6181 | 194 | 8
94 | 235 | NE | Creelman | 235 | EOC |  |  |  | 14.8273 | 1.5499 | 203 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 2 | 2 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.22982 | 117 | 10.4537 | 229 |  |  | 1.5499 | 203 | 0 | 1.7662 | 135 | 68 | 1.5559 | 199 | 4 | 1.4932 | 213 | 10
159 | 411 | EA | Granite | P172406 | 411-14R |  |  |  | 1.8231 | 1.53 | 204 | 1 | 1 | 0 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 1 | 2 | 2 |  |  | 0.027894 | 256 | 83.9227 | 20 |  |  | 1.53 | 204 | 0 | 1.4436 | 214 | 10 | 1.6184 | 173 | 31 | 1.4847 | 215 | 11
255 | 972 | NE | Creelman | 972 | 972-7 | 972-4 |  |  | 7.2384 | 1.5299 | 205 | 1 | 2 | 2 | 1 | 1 | 1 | 3 | 3 | 1 | 2 | 0 | 1 | 3 | 2 | 2 | 1 | 1 |  |  | 0.11075 | 187 | 21.1371 | 123 |  |  | 1.5299 | 205 | 0 | 1.6496 | 164 | 41 | 1.5414 | 204 | 1 | 1.4925 | 214 | 9
230 | 597 | NE | San Marcos | 597-35 | 597-636 |  |  |  | 4.582 | 1.52 | 206 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 3 | 1 | 2 | 1 |  |  | 0.069647 | 216 | 33.1732 | 75 |  |  | 1.52 | 206 | 0 | 1.4631 | 207 | 1 | 1.5921 | 184 | 22 | 1.4798 | 218 | 12
118 | 283 | EA | Loveland | 283-29 | 283-26 |  |  |  | 8.5809 | 1.5199 | 207 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 2 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 1 | 2 |  |  | 0.13043 | 174 | 17.7138 | 149 |  |  | 1.5199 | 207 | 0 | 1.4362 | 215 | 8 | 1.4808 | 215 | 8 | 1.5693 | 197 | 10
45 | 204 | OC | San Mateo | 204-6 | EOC |  |  |  | 8.9962 | 1.5199 | 208 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.13674 | 169 | 16.896 | 157 |  |  | 1.5199 | 208 | 0 | 1.5042 | 200 | 8 | 1.5767 | 190 | 18 | 1.4813 | 216 | 8
7 | 75 | EA | Jamacha | 75-40 | 75-32R |  |  |  | 10.9716 | 1.5199 | 209 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 2 | 3 | 1 | 1 |  |  | 0.16677 | 154 | 13.854 | 188 |  |  | 1.5199 | 209 | 0 | 1.6186 | 173 | 36 | 1.5542 | 200 | 9 | 1.4705 | 219 | 10
44 | 204 | OC | San Mateo | 204-2 | 204-6 |  |  |  | 12.6553 | 1.5199 | 210 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.19236 | 136 | 12.0108 | 211 |  |  | 1.5199 | 210 | 0 | 1.5042 | 201 | 9 | 1.5766 | 191 | 19 | 1.4812 | 217 | 7
119 | 283 | EA | Loveland | 283-26 | EOC |  |  |  | 4.7106 | 1.51 | 211 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.07113 | 214 | 32.0553 | 77 |  |  | 1.51 | 211 | 0 | 1.4558 | 211 | 0 | 1.4546 | 219 | 8 | 1.5643 | 199 | 12
315 | SSC1 | OC | So San Clemente | SSC1 | SSC1-3 |  |  |  | 1.1203 | 1.5 | 212 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 |  |  | 0.016804 | 270 | 133.8969 | 11 |  |  | 1.5 | 212 | 0 | 1.3104 | 231 | 19 | 1.49 | 210 | 2 | 1.5532 | 203 | 9
62 | 214 | NE | Rincon | 214 | 214-10 | 214-7 |  |  | 8.1002 | 1.4899 | 213 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 3 | 1 | 1 |  |  | 0.12069 | 179 | 18.3946 | 141 |  |  | 1.4899 | 213 | 0 | 1.5215 | 198 | 15 | 1.5133 | 207 | 6 | 1.4649 | 221 | 8
129 | 327 | NE | Warren Canyon | 327 | EOC |  |  |  | 0.88636 | 1.48 | 214 | 1 | 2 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 | 3 | 1 |  |  | 0.013118 | 273 | 166.9744 | 8 |  |  | 1.48 | 214 | 0 | 1.1433 | 253 | 39 | 1.5144 | 206 | 8 | 1.5354 | 205 | 9
286 | 1138 | EA | Santee | 1138-22 | EOC |  |  |  | 2.4225 | 1.48 | 215 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.035854 | 249 | 61.093 | 30 |  |  | 1.48 | 215 | 0 | 1.3906 | 221 | 6 | 1.422 | 229 | 14 | 1.5448 | 204 | 11
293 | 1235 | NE | Monserate | 1235 | EOC |  |  |  | 16.8837 | 1.4798 | 216 | 1 | 2 | 3 | 1 | 1 | 0 | 3 | 2 | 2 | 3 | 0 | 2 | 0 | 2 | 1 | 1 | 1 |  |  | 0.24988 | 102 | 8.7658 | 247 |  |  | 1.4798 | 216 | 0 | 1.4224 | 219 | 3 | 1.4302 | 227 | 11 | 1.5308 | 206 | 10
189 | 454 | NE | Ash | 454-15 | EOC |  |  |  | 3.7525 | 1.47 | 217 | 1 | 1 | 1 | 3 | 3 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 1 | 1 |  |  | 0.055161 | 231 | 39.1743 | 64 |  |  | 1.47 | 217 | 0 | 1.2503 | 237 | 20 | 1.3544 | 246 | 29 | 1.6092 | 196 | 21
79 | 221 | NE | Santa Ysabel | P478409 | EOC |  |  |  | 23.4551 | 1.4698 | 218 | 1 | 3 | 0 | 1 | 2 | 0 | 1 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 0.34479 | 60 | 6.2673 | 270 |  |  | 1.4698 | 218 | 0 | 1.5283 | 197 | 21 | 1.4523 | 221 | 3 | 1.4687 | 220 | 2
214 | 522 | NE | Avocado | 522 | 522-25 |  |  |  | 5.5396 | 1.4599 | 219 | 1 | 2 | 2 | 1 | 1 | 0 | 2 | 3 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.080878 | 204 | 26.3558 | 98 |  |  | 1.4599 | 219 | 0 | 1.5387 | 191 | 28 | 1.4499 | 222 | 3 | 1.4484 | 222 | 3
198 | 502 | NE | Chicarita | 502-28 | EOC |  |  |  | 1.3011 | 1.45 | 220 | 1 | 1 | 1 | 3 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 | 2 | 2 |  |  | 0.018866 | 267 | 111.441 | 16 |  |  | 1.45 | 220 | 0 | 1.0781 | 260 | 40 | 1.4818 | 213 | 7 | 1.5159 | 209 | 11
42 | 204 | OC | San Mateo | 204 | 204-24 | 204-2 | EOC |  | 6.3936 | 1.4499 | 221 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.092707 | 195 | 22.6791 | 118 |  |  | 1.4499 | 221 | 0 | 1.3521 | 227 | 6 | 1.5006 | 208 | 13 | 1.4357 | 223 | 2
85 | 230 | NE | Monserate | 230-4R | 230-133 |  |  |  | 7.039 | 1.4499 | 222 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.10207 | 190 | 20.5995 | 126 |  |  | 1.4499 | 222 | 0 | 1.5489 | 190 | 32 | 1.4473 | 224 | 2 | 1.428 | 226 | 4
127 | 315 | OC | Capistrano | 315-2 | 315-502 |  |  |  | 5.84 | 1.4399 | 223 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 1 |  |  | 0.084095 | 201 | 24.6577 | 108 |  |  | 1.4399 | 223 | 0 | 1.3303 | 229 | 6 | 1.4898 | 211 | 12 | 1.4291 | 225 | 2
18 | 91 | EA | Jamacha | Z971734 | 91-649 |  |  |  | 0.84886 | 1.43 | 224 | 1 | 3 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 |  |  | 0.012139 | 274 | 168.4605 | 7 |  |  | 1.43 | 224 | 0 | 1.1675 | 250 | 26 | 1.3902 | 237 | 13 | 1.523 | 208 | 16
263 | 975 | NE | Creelman | 975 | 975-2 |  |  |  | 4.1525 | 1.43 | 225 | 1 | 2 | 1 | 1 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 2 | 2 |  |  | 0.05938 | 225 | 34.4374 | 71 |  |  | 1.43 | 225 | 0 | 1.2314 | 242 | 17 | 1.4067 | 234 | 9 | 1.4952 | 212 | 13
33 | 185 | NE | Escondido | P417773 | EOC |  |  |  | 5.4458 | 1.4199 | 226 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.077331 | 207 | 26.075 | 100 |  |  | 1.4199 | 226 | 0 | 1.4517 | 212 | 14 | 1.4065 | 235 | 9 | 1.4224 | 227 | 1
312 | RC1 | NE | Reidy Canyon | RC1 | EOC |  |  |  | 2.6373 | 1.41 | 227 | 1 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 2 |  |  | 0.037186 | 246 | 53.4636 | 34 |  |  | 1.41 | 227 | 0 | 1.0787 | 259 | 32 | 1.3046 | 253 | 26 | 1.5685 | 198 | 29
111 | 246 | EA | Los Coches | 246-11 | EOC |  |  |  | 9.2875 | 1.3999 | 228 | 1 | 1 | 2 | 1 | 1 | 0 | 3 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 0.13003 | 175 | 15.074 | 171 |  |  | 1.3999 | 228 | 0 | 1.5586 | 188 | 40 | 1.4497 | 223 | 5 | 1.3244 | 241 | 13
86 | 230 | NE | Monserate | 230-11 | EOC |  |  |  | 10.4443 | 1.3999 | 229 | 1 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 1 | 3 | 3 | 1 | 1 | 1 |  |  | 0.14622 | 161 | 13.4044 | 195 |  |  | 1.3999 | 229 | 0 | 1.435 | 216 | 13 | 1.4959 | 209 | 20 | 1.3197 | 242 | 13
190 | 455 | NE | Ash | 455-979 | 455-34 | EOC |  |  | 4.0966 | 1.39 | 230 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 0.056943 | 229 | 33.9307 | 73 |  |  | 1.39 | 230 | 0 | 1.4278 | 218 | 12 | 1.3585 | 245 | 15 | 1.4044 | 229 | 1
299 | FB1 | NE | Fallbrook 1 | FB1 | EOC |  |  |  | 4.1939 | 1.39 | 231 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 2 | 1 | 1 | 1 |  |  | 0.058296 | 227 | 33.1431 | 76 |  |  | 1.39 | 231 | 0 | 1.3865 | 222 | 9 | 1.3739 | 242 | 11 | 1.4028 | 231 | 0
134 | 339 | OC | Cristianitos | 339 | EOC |  |  |  | 9.4475 | 1.3899 | 232 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 2 | 2 |  |  | 0.13132 | 173 | 14.7128 | 176 |  |  | 1.3899 | 232 | 0 | 1.1392 | 255 | 23 | 1.4662 | 218 | 14 | 1.3934 | 235 | 3
121 | 300 | NC | Pendleton | 300-1 | 300-25 | EOC |  |  | 11.622 | 1.3899 | 233 | 1 | 2 | 1 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 0.16155 | 155 | 11.9601 | 213 |  |  | 1.3899 | 233 | 0 | 1.2309 | 243 | 10 | 1.4117 | 233 | 0 | 1.4119 | 228 | 5
116 | 260 | CM | Otay Lakes | 260 | EOC |  |  |  | 12.5536 | 1.3899 | 234 | 1 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 2 | 1 | 0 | 3 | 0 | 2 | 1 | 3 | 3 |  |  | 0.1745 | 146 | 11.0725 | 224 |  |  | 1.3899 | 234 | 0 | 1.3813 | 224 | 10 | 1.4767 | 216 | 18 | 1.3271 | 240 | 6
40 | 202 | NC | Las Pulgas | 202 | EOC |  |  |  | 12.603 | 1.3899 | 235 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 0.17518 | 145 | 11.0291 | 225 |  |  | 1.3899 | 235 | 0 | 1.2628 | 234 | 1 | 1.42 | 231 | 4 | 1.398 | 232 | 3
309 | RA3 | NE | Ramona | RA3 | EOC |  |  |  | 3.068 | 1.38 | 236 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 0.042338 | 240 | 44.9806 | 54 |  |  | 1.38 | 236 | 0 | 1.406 | 220 | 16 | 1.3476 | 248 | 12 | 1.3979 | 233 | 3
188 | 452 | NE | Ash | 452-748 | EOC |  |  |  | 4.5273 | 1.38 | 237 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 2 | 1 |  |  | 0.062476 | 221 | 30.4819 | 80 |  |  | 1.38 | 237 | 0 | 1.3236 | 230 | 7 | 1.3784 | 241 | 4 | 1.3947 | 234 | 3
130 | 329 | OC | San Mateo | 329 | EOC |  |  |  | 4.5527 | 1.38 | 238 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 2 | 1 |  |  | 0.062827 | 220 | 30.312 | 83 |  |  | 1.38 | 238 | 0 | 1.168 | 249 | 11 | 1.4163 | 232 | 6 | 1.4039 | 230 | 8
30 | 182 | NE | Escondido | 182-354 | P510606 | Z16125 | EOC |  | 10.4362 | 1.3799 | 239 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 2 | 1 | 1 | 3 | 2 | 1 | 1 | 3 |  |  | 0.14402 | 162 | 13.2232 | 198 |  |  | 1.3799 | 239 | 0 | 1.4739 | 205 | 34 | 1.4434 | 225 | 14 | 1.3098 | 245 | 6
300 | FB2 | NE | Fallbrook 2 | FB2 | EOC |  |  |  | 3.8405 | 1.37 | 240 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 0.052615 | 233 | 35.6722 | 68 |  |  | 1.37 | 240 | 0 | 1.3843 | 223 | 17 | 1.3367 | 249 | 9 | 1.3913 | 237 | 3
234 | 728 | BC | Scripps | 728-689 | EOC |  |  |  | 2.086 | 1.36 | 241 | 1 | 1 | 0 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 0 | 3 | 1 | 3 | 1 |  |  | 0.028369 | 254 | 65.197 | 26 |  |  | 1.36 | 241 | 0 | 1.2337 | 240 | 1 | 1.475 | 217 | 24 | 1.3045 | 247 | 6
122 | 300 | NC | Pendleton | 300-25 | EOC |  |  |  | 5.5492 | 1.3599 | 242 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 0.07547 | 210 | 24.5078 | 109 |  |  | 1.3599 | 242 | 0 | 1.1657 | 251 | 9 | 1.3791 | 240 | 2 | 1.3924 | 236 | 6
216 | 523 | NE | Avocado | 523 | 523-31AE |  |  |  | 3.7097 | 1.35 | 243 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.05008 | 236 | 36.3915 | 66 |  |  | 1.35 | 243 | 0 | 1.4593 | 210 | 33 | 1.3718 | 243 | 0 | 1.3073 | 246 | 3
270 | 1001 | NC | Rancho Santa Fe | P132166 | EOC |  |  |  | 2.1189 | 1.32 | 244 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 1 |  |  | 0.02797 | 255 | 62.2953 | 29 |  |  | 1.32 | 244 | 0 | 1.2199 | 244 | 0 | 1.4244 | 228 | 16 | 1.2661 | 254 | 10
38 | 200 | OC | San Mateo | 200 | 200-29 | EOC |  |  | 3.1027 | 1.32 | 245 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 2 | 3 | 1 |  |  | 0.040955 | 242 | 42.5443 | 58 |  |  | 1.32 | 245 | 0 | 1.2652 | 233 | 12 | 1.4883 | 212 | 33 | 1.2074 | 257 | 12
123 | 307 | NC | Rancho Santa Fe | P230241 | EOC |  |  |  | 0.7428 | 1.31 | 246 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 1 | 1 |  |  | 0.0097307 | 279 | 176.359 | 5 |  |  | 1.31 | 246 | 0 | 1.2075 | 246 | 0 | 1.3899 | 238 | 8 | 1.275 | 249 | 3
308 | RA2 | NE | Ramona | RA2 | EOC |  |  |  | 2.8767 | 1.31 | 247 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 0.037685 | 245 | 45.5382 | 52 |  |  | 1.31 | 247 | 0 | 1.2539 | 236 | 11 | 1.2715 | 258 | 11 | 1.3522 | 238 | 9
43 | 204 | OC | San Mateo | 204-24 | EOC |  |  |  | 5.0672 | 1.3099 | 248 | 1 | 1 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 0.066381 | 218 | 25.8524 | 102 |  |  | 1.3099 | 248 | 0 | 1.2074 | 247 | 1 | 1.3898 | 239 | 9 | 1.275 | 250 | 2
191 | 455 | NE | Ash | 455-926 | 455-34 | EOC |  |  | 1.7877 | 1.3 | 249 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 0 | 1 | 1 |  |  | 0.02324 | 262 | 72.7196 | 24 |  |  | 1.3 | 249 | 0 | 1.2321 | 241 | 8 | 1.2607 | 259 | 10 | 1.3457 | 239 | 10
217 | 523 | NE | Avocado | 523-31AE | EOC |  |  |  | 2.7553 | 1.3 | 250 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 0.035819 | 250 | 47.1817 | 47 |  |  | 1.3 | 250 | 0 | 1.3506 | 228 | 22 | 1.3174 | 251 | 1 | 1.2747 | 251 | 1
124 | 307 | NC | Rancho Santa Fe | Z12392 | EOC |  |  |  | 5.7 | 1.2899 | 251 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 2 |  |  | 0.07353 | 213 | 22.6316 | 119 |  |  | 1.2899 | 251 | 0 | 1.2412 | 238 | 13 | 1.4403 | 226 | 25 | 1.1894 | 260 | 9
283 | 1101 | NE | Artesian | 1101-1 | P819071 |  |  |  | 3.0506 | 1.28 | 252 | 1 | 2 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 3 | 1 |  |  | 0.039047 | 243 | 41.9594 | 60 |  |  | 1.28 | 252 | 0 | 1.0691 | 261 | 9 | 1.3644 | 244 | 8 | 1.2677 | 253 | 1
49 | 209 | NC | Melrose | P214248 | EOC |  |  |  | 2.4578 | 1.25 | 253 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 2 | 1 | 1 |  |  | 0.030722 | 252 | 50.8592 | 35 |  |  | 1.25 | 253 | 0 | 1.041 | 264 | 11 | 1.2371 | 260 | 7 | 1.31 | 244 | 9
132 | 331 | OC | San Mateo | 331-2 | EOC |  |  |  | 2.8953 | 1.25 | 254 | 1 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 1 |  |  | 0.036191 | 248 | 43.1739 | 57 |  |  | 1.25 | 254 | 0 | 0.88539 | 280 | 26 | 1.275 | 256 | 2 | 1.3191 | 243 | 11
112 | 247 | EA | Los Coches | 247-14 | P33699 |  |  |  | 5.5227 | 1.2399 | 255 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 3 | 2 | 2 | 1 | 1 |  |  | 0.068482 | 217 | 22.4527 | 121 |  |  | 1.2399 | 255 | 0 | 1.3706 | 225 | 30 | 1.3172 | 252 | 3 | 1.1507 | 263 | 8
34 | 188 | NE | Escondido | P216702 | EOC |  |  |  | 0.9428 | 1.23 | 256 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 1 | 1 |  |  | 0.011596 | 275 | 130.462 | 12 |  |  | 1.23 | 256 | 0 | 1.0387 | 265 | 9 | 1.2 | 267 | 11 | 1.2985 | 248 | 8
222 | 536 | CM | Border | Z135595 | EOC |  |  |  | 3.3883 | 1.23 | 257 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 1 | 1 | 1 | 2 | 3 |  |  | 0.041676 | 241 | 36.3018 | 67 |  |  | 1.23 | 257 | 0 | 1.2396 | 239 | 18 | 1.226 | 264 | 7 | 1.2306 | 256 | 1
89 | 232 | NE | Monserate | 232 | EOC |  |  |  | 4.967 | 1.21 | 258 | 1 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.060101 | 223 | 24.3606 | 110 |  |  | 1.21 | 258 | 0 | 1.1869 | 248 | 10 | 1.2279 | 263 | 5 | 1.2021 | 258 | 0
221 | 527 | OC | Las Pulgas | 527 | EOC |  |  |  | 6.2663 | 1.1899 | 259 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3 | 3 |  |  | 0.074569 | 211 | 18.9905 | 136 |  |  | 1.1899 | 259 | 0 | 0.95173 | 271 | 12 | 1.1564 | 273 | 14 | 1.2724 | 252 | 7
37 | 198 | NC | San Luis Rey | 198-4 | P121327 | Z29143 |  |  | 0.48769 | 1.18 | 260 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 3 | 3 |  |  | 0.0057547 | 283 | 241.9573 | 2 |  |  | 1.18 | 260 | 0 | 0.91971 | 275 | 15 | 1.3515 | 247 | 13 | 1.1146 | 266 | 6
133 | 338 | OC | Cristianitos | 338 | EOC |  |  |  | 0.91439 | 1.18 | 261 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 1 |  |  | 0.01079 | 276 | 129.0472 | 13 |  |  | 1.18 | 261 | 0 | 0.96609 | 270 | 9 | 1.2332 | 261 | 0 | 1.1918 | 259 | 2
224 | 542 | NE | Bernardo | 542 | 542-13 |  |  |  | 1.8415 | 1.18 | 262 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 2 | 2 |  |  | 0.021729 | 264 | 64.079 | 28 |  |  | 1.18 | 262 | 0 | 0.91559 | 276 | 14 | 1.2722 | 257 | 5 | 1.1748 | 262 | 0
237 | 791 | NE | Felicita | 791-26 | EOC |  |  |  | 4.943 | 1.18 | 263 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 0 | 3 | 0 | 2 | 1 |  |  | 0.058327 | 226 | 23.8722 | 113 |  |  | 1.18 | 263 | 0 | 1.1165 | 256 | 7 | 1.2982 | 254 | 9 | 1.1069 | 268 | 5
282 | 1100 | NE | Artesian | P515154 | EOC |  |  |  | 1.2008 | 1.17 | 264 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 0.014049 | 272 | 97.4385 | 17 |  |  | 1.17 | 264 | 0 | 0.94952 | 272 | 8 | 1.1194 | 277 | 13 | 1.2609 | 255 | 9
36 | 197 | OC | Capistrano | 197-19 | EOC |  |  |  | 1.4297 | 1.17 | 265 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 3 | 2 |  |  | 0.016728 | 271 | 81.8334 | 21 |  |  | 1.17 | 265 | 0 | 0.93918 | 273 | 8 | 1.3253 | 250 | 15 | 1.1096 | 267 | 2
281 | 1100 | NE | Artesian | 1100 | 1100-46 | EOC |  |  | 2.458 | 1.17 | 266 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 3 | 1 |  |  | 0.028758 | 253 | 47.6006 | 46 |  |  | 1.17 | 266 | 0 | 1.0268 | 266 | 0 | 1.1915 | 268 | 2 | 1.1884 | 261 | 5
31 | 182 | NE | Escondido | P510606 | P810041 | P113377 | EOC |  | 6.4737 | 1.1699 | 267 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 0.075742 | 209 | 18.0732 | 148 |  |  | 1.1699 | 267 | 0 | 1.2596 | 235 | 32 | 1.2258 | 265 | 2 | 1.1066 | 269 | 2
39 | 200 | OC | San Mateo | 200-28 | 200-6 | 200-438 |  |  | 0.4553 | 1.12 | 268 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 3 | 2 | 1 | 1 |  |  | 0.0050994 | 286 | 245.99 | 1 |  |  | 1.12 | 268 | 0 | 1.1046 | 257 | 11 | 1.2898 | 255 | 13 | 0.99686 | 281 | 13
48 | 206 | NC | Melrose | 206-1105 | EOC |  |  |  | 4.8136 | 1.12 | 269 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 3 | 2 | 1 | 1 | 1 |  |  | 0.053913 | 232 | 23.2672 | 116 |  |  | 1.12 | 269 | 0 | 1.1509 | 252 | 17 | 1.1714 | 270 | 1 | 1.074 | 273 | 4
128 | 315 | OC | Capistrano | 315-501 | EOC |  |  |  | 0.47576 | 1.11 | 270 | 1 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 2 |  |  | 0.0052809 | 284 | 233.3121 | 3 |  |  | 1.11 | 270 | 0 | 0.89119 | 278 | 8 | 1.2293 | 262 | 8 | 1.0736 | 274 | 4
223 | 540 | NE | Bernardo | 540 | 540-2 |  |  |  | 0.95871 | 1.11 | 271 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 2 | 1 |  |  | 0.010642 | 277 | 115.7803 | 15 |  |  | 1.11 | 271 | 0 | 0.96951 | 269 | 2 | 1.1192 | 278 | 7 | 1.137 | 264 | 7
106 | 242 | EA | Los Coches | 242 | 241-T6-242 |  |  |  | 2.3888 | 1.11 | 272 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 1 |  |  | 0.026516 | 258 | 46.4663 | 51 |  |  | 1.11 | 272 | 0 | 1.088 | 258 | 14 | 1.176 | 269 | 3 | 1.066 | 275 | 3
249 | 970 | NE | Creelman | 970 | 970-10 |  |  |  | 2.2697 | 1.09 | 273 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 2 | 0 | 3 | 2 |  |  | 0.02474 | 259 | 48.024 | 43 |  |  | 1.09 | 273 | 0 | 1.0033 | 267 | 6 | 1.1696 | 271 | 2 | 1.0514 | 276 | 3
32 | 185 | NE | Escondido | P114604 | EOC |  |  |  | 0.88409 | 1.08 | 274 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 0.0095482 | 280 | 122.1594 | 14 |  |  | 1.08 | 274 | 0 | 1.064 | 262 | 12 | 1.128 | 274 | 0 | 1.048 | 277 | 3
107 | 242 | EA | Los Coches | P970731 | EOC |  |  |  | 1.7996 | 1.08 | 275 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 0.019436 | 265 | 60.0126 | 31 |  |  | 1.08 | 275 | 0 | 1.064 | 263 | 12 | 1.128 | 275 | 0 | 1.048 | 278 | 3
115 | 252 | BC | Kearny | P36981 | EOC |  |  |  | 4.1129 | 1.08 | 276 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 1 | 3 | 3 | 3 |  |  | 0.044419 | 239 | 26.259 | 99 |  |  | 1.08 | 276 | 0 | 1.1412 | 254 | 22 | 1.2001 | 266 | 10 | 0.97543 | 282 | 6
236 | 776 | BC | Mesa Heights | 776-8 | EOC |  |  |  | 2.1811 | 1.07 | 277 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 3 | 1 |  |  | 0.023337 | 261 | 49.0587 | 38 |  |  | 1.07 | 277 | 0 | 0.93304 | 274 | 3 | 1.0367 | 279 | 2 | 1.1279 | 265 | 12
229 | 594 | CM | Proctor Valley | P166873 | EOC |  |  |  | 1.8324 | 1.06 | 278 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 3 | 0 | 2 | 0 | 3 | 1 |  |  | 0.019423 | 266 | 57.8481 | 32 |  |  | 1.06 | 278 | 0 | 0.97929 | 268 | 10 | 1.1216 | 276 | 2 | 1.0334 | 279 | 1
41 | 203 | OC | San Mateo | 203 | 203-7 |  |  |  | 2.5756 | 1.06 | 279 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 1 | 1 |  |  | 0.027301 | 257 | 41.156 | 62 |  |  | 1.06 | 279 | 0 | 0.85563 | 282 | 3 | 1.1678 | 272 | 7 | 1.0287 | 280 | 1
47 | 205 | NC | Melrose | P116036 | EOC |  |  |  | 0.4911 | 1.04 | 280 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 1 |  |  | 0.0051074 | 285 | 211.7702 | 4 |  |  | 1.04 | 280 | 0 | 0.85856 | 281 | 1 | 1.0277 | 280 | 0 | 1.0929 | 272 | 8
313 | SE4 | OC | Serra | SE4 | EOC |  |  |  | 0.59299 | 1.03 | 281 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 1 |  |  | 0.0061078 | 282 | 173.6953 | 6 |  |  | 1.03 | 281 | 0 | 0.80488 | 285 | 4 | 1.0086 | 281 | 0 | 1.1002 | 271 | 10
248 | 968 | BC | Eastgate | 968-14 | EOC |  |  |  | 2.1536 | 1.03 | 282 | 1 | 1 | 0 | 2 | 2 | 1 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 |  |  | 0.022182 | 263 | 47.8269 | 44 |  |  | 1.03 | 282 | 0 | 0.8873 | 279 | 3 | 0.97779 | 283 | 1 | 1.1033 | 270 | 12
46 | 205 | NC | Melrose | P111778 | EOC |  |  |  | 0.70625 | 0.95999 | 283 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 1 |  |  | 0.00678 | 281 | 135.9292 | 10 |  |  | 0.95999 | 283 | 0 | 0.84434 | 283 | 0 | 0.98217 | 282 | 1 | 0.9713 | 284 | 1
235 | 770 | BC | Mesa Heights | Z90080 | EOC |  |  |  | 1.8898 | 0.93998 | 284 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3 | 1 |  |  | 0.017764 | 268 | 49.7414 | 37 |  |  | 0.93998 | 284 | 0 | 0.81013 | 284 | 0 | 0.93675 | 284 | 0 | 0.97369 | 283 | 1
192 | 463 | CM | San Ysidro | P108483 | EOC |  |  |  | 1.9051 | 0.92998 | 285 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 1 |  |  | 0.017718 | 269 | 48.816 | 39 |  |  | 0.92998 | 285 | 0 | 0.90276 | 277 | 8 | 0.90337 | 285 | 0 | 0.95642 | 285 | 0
131 | 330 | OC | San Mateo | 330-10 | P25224 |  |  |  | 1.4953 | 0.67999 | 286 | 1 | 2 | 1 | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  |  | 0.010168 | 278 | 45.4769 | 53 |  |  | 0.67999 | 286 | 0 | 0.72508 | 286 | 0 | 0.59607 | 286 | 0 | 0.7318 | 286 | 0
| A | Circuit | bar: Environment 1
| B | Study segment boundaries | bar: Environment 1
| C | Length in miles of the study segment | bar: Environment 1
| D | Weighted score | bar: Environment 1
| E | Ranking | bar: Environment 1
| 1 | Risk zone: HRFA: 3, FTZ: 1
| 2 | Wind Factor: Based on the forecasted frequency of extreme wind events - (Brian D'Agostino)
| 3 | Tree Factor: Density of trees in proximity that are >=40ft weighted by species (Vegetation Management)
| 4 | Fuel: (Fire Coordinator)
| 5 | Fire ignition risk: (Fire Coordinator)
| 6 | Capacitor factor - number of capacitors in segment (TDAM) | bar: Environment 1
| 7 | Expulsion fuse factor (TDAM) | bar: Environment 1
| 8 | Switch factor (TDAM) | bar: Environment 1
| 9 | Conductor factor -smaller than 2/0- (TDAM) | bar: Environment 1
| 10 | Transformer factor (TDAM) | bar: Environment 1
| 11 | High-risk transformer factor (TDAM) | bar: Environment 1
| 12 | Ranking by district operating center | bar: Environment 1
| 13 | 5-Year Outage History Index (TDAM) | bar: Environment 1
| 14 | Relative structure value in projected burn path (Fire Coordinator) | bar: Environment 1
| 15 | Reduction in the number of customers impacted by 2012 safety shut off plan (TDAM) | bar: Environment 1
| 16 | Service to critical facilities, water, communication, health, public protection (TDAM, CISCO) | bar: Environment 1
| 17 | Ranking by environmental | bar: Environment 1
| 18 | Ranking by cultural | bar: Environment 1
Italic = open switch (tie or fuse bypass)