## Data
MGRA DR-03 Q66
Outages Occuring On Previously Identified Circuits (1981-2014)
| Circuit | Occurrence | Cause Category | Cause Description | Control Date | Station Code
| 1001 | 2005-01-10 05:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 1001 | 2005-02-21 07:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 1001 | 2005-07-20 20:04 | Customer Contact | Vehicle contact | 0 | RSF
| 1001 | 2005-08-25 11:24 | Customer Contact | Vehicle contact | 0 | RSF
| 1001 | 2006-01-13 08:32 | Undetermined | Undetermined | 0 | RSF
| 1001 | 2006-10-14 11:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 1001 | 2006-10-14 16:04 | Customer Contact | Vehicle contact | 0 | RSF
| 1001 | 2006-12-27 06:31 | Equipment | Capacitor failure | 0 | RSF
| 1001 | 2007-08-16 15:28 | Undetermined | Undetermined | 0 | RSF
| 1001 | 2009-06-03 09:32 | Weather | Lightning Arrester/Transformer failure | 0 | RSF
| 1001 | 2009-08-15 13:07 | Equipment | Conductor failure/wire down | 0 | RSF
| 1001 | 2009-12-07 16:28 | Weather | Tree fell on line due to storm/wind | 0 | RSF
| 1001 | 2010-05-08 22:31 | Customer Contact | Vehicle contact | 0 | RSF
| 1001 | 2010-05-12 19:37 | Undetermined | Undetermined | 0 | RSF
| 1001 | 2010-11-24 06:00 | Customer Contact | Vehicle contact | 0 | RSF
| 1001 | 2010-12-23 01:48 | Weather | Tree fell on line due to storm/wind | 0 | RSF
| 1001 | 2010-12-23 23:40 | Equipment | Conductor failure/wire down | 0 | RSF
| 1001 | 2011-03-20 11:17 | Weather | Ice or snow/Equipment failure | 0 | RSF
| 1001 | 2011-05-17 20:44 | Foreign Object | Bird contact | 0 | RSF
| 1001 | 2012-02-27 23:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 1001 | 2014-04-09 06:57 | Customer Contact | Vehicle contact | 0 | RSF
| 1001 | 2014-05-19 12:48 | Undetermined | Undetermined | 0 | RSF
| 1001 | 2014-11-07 01:23 | Equipment | Pole broke/rotted/on fire | 0 | RSF
| 1001 | 2014-12-02 07:43 | Foreign Object | Bird contact | 0 | RSF
| 1001 | 2015-01-16 18:50 | Undetermined | Undetermined | 0 | RSF
| 1021 | 2010-01-04 16:57 | Foreign Object | Bird contact | 0 | HID
| 1021 | 2010-09-08 09:24 | Equipment | Fuse holder/fuse cabinet failed | 0 | HID
| 1021 | 2010-09-30 13:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 1021 | 2010-09-30 18:12 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 1021 | 2010-10-21 00:03 | Equipment | Arrester (lightning) failure | 0 | HID
| 1021 | 2010-10-21 01:33 | Equipment | Arrester (lightning) failure | 0 | HID
| 1021 | 2010-12-24 22:23 | Equipment | Transformer faulted/mechanical | 0 | HID
| 1021 | 2011-02-02 01:13 | Weather | Wind - wires slap/pole down | 0 | HID
| 1021 | 2012-01-30 07:23 | Foreign Object | Bird contact | 0 | HID
| 1021 | 2012-02-09 15:04 | Equipment | Arrester (lightning) failure | 0 | HID
| 1021 | 2012-09-09 18:04 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 1021 | 2012-11-06 12:44 | Equipment | Cutout failure | 0 | HID
| 1021 | 2012-12-13 03:48 | Foreign Object | Flashover/vegetation | 0 | HID
| 1021 | 2013-01-30 01:20 | Foreign Object | Bird contact | 0 | HID
| 1021 | 2013-02-13 11:30 | Equipment | Pole broke/rotted/on fire | 0 | HID
| 1021 | 2013-08-27 13:04 | Equipment | Transformer faulted/mechanical | 0 | HID
| 1021 | 2013-10-06 12:59 | Undetermined | Undetermined | 0 | HID
| 1021 | 2013-10-30 18:08 | Equipment | Transformer faulted/mechanical | 0 | HID
| 1021 | 2014-07-18 21:32 | Undetermined | Undetermined | 0 | HID
| 1021 | 2014-10-01 13:01 | Undetermined | Undetermined | 0 | HID
| 1030 | 2005-01-22 08:42 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2005-05-15 03:01 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2005-05-20 04:06 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2005-06-04 09:24 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2005-07-23 02:01 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2005-07-23 02:05 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2005-07-23 02:08 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2005-10-16 18:07 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2005-12-03 11:24 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2006-07-02 05:50 | Foreign Object | Bird contact | 1 | HHC
| 1030 | 2006-08-12 14:24 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2006-10-15 15:31 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2006-12-31 16:40 | Foreign Object | Bird contact | 0 | HHC
| 1030 | 2006-12-31 19:09 | Foreign Object | Bird contact | 0 | HHC
| 1030 | 2007-03-13 10:40 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2007-03-22 17:02 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2007-04-24 16:34 | Equipment | Transformer faulted/mechanical | 0 | HHC
| 1030 | 2007-06-21 05:42 | Foreign Object | Bird contact | 0 | HHC
| 1030 | 2007-07-14 02:48 | Customer Contact | Vehicle contact | 1 | HHC
| 1030 | 2007-08-25 14:18 | Foreign Object | Foreign object in distribution line | 0 | HHC
| 1030 | 2007-08-26 06:45 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2007-08-26 07:36 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2007-08-26 08:50 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2007-08-26 12:45 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2007-09-30 05:50 | Equipment | Conductor failure/wire down | 0 | HHC
| 1030 | 2007-10-16 14:06 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2007-10-22 00:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC
| 1030 | 2007-10-22 00:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC
| 1030 | 2007-10-22 02:06 | Weather | Wind - wires slap/pole down | 0 | HHC
| 1030 | 2008-01-03 11:46 | Equipment | Crossarm failure | 0 | HHC
| 1030 | 2008-03-09 18:12 | Foreign Object | Foreign object in distribution line | 0 | HHC
| 1030 | 2008-03-20 11:53 | Customer Contact | Heavy equp contact/digin | 0 | HHC
| 1030 | 2008-05-22 13:31 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2008-07-08 19:19 | Foreign Object | Bird contact | 1 | HHC
| 1030 | 2008-08-20 23:46 | Foreign Object | Damage by gunshot | 0 | HHC
| 1030 | 2008-11-04 00:14 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2008-11-25 12:20 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2009-01-26 23:22 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2009-04-13 17:00 | Equipment | Arrester (lightning) failure | 0 | HHC
| 1030 | 2009-04-16 12:33 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2009-05-29 05:15 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2009-12-07 05:25 | Weather | Palm frond contact due to storm/wind | 0 | HHC
| 1030 | 2010-01-18 16:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC
| 1030 | 2010-05-26 17:46 | Foreign Object | Bird contact | 0 | HHC
| 1030 | 2010-12-22 07:11 | Weather | Tree fell on line due to storm/wind | 0 | HHC
| 1030 | 2010-12-29 14:37 | Weather | Tree fell on line due to storm/wind | 0 | HHC
| 1030 | 2011-01-15 22:16 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2011-01-23 05:20 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2011-02-09 09:22 | Equipment | Conductor contact/wire slap | 0 | HHC
| 1030 | 2011-02-14 22:50 | Equipment | Conductor failure/wire down | 0 | HHC
| 1030 | 2011-05-31 09:41 | Equipment | Fuse holder/fuse cabinet failed | 0 | HHC
| 1030 | 2011-06-14 02:19 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2011-07-30 12:01 | Foreign Object | Bird contact | 0 | HHC
| 1030 | 2011-09-03 18:41 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2011-09-27 14:15 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2011-11-02 08:09 | Weather | Wind - wires slap/pole down | 0 | HHC
| 1030 | 2011-11-09 23:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC
| 1030 | 2011-11-16 06:33 | Foreign Object | Bird contact | 0 | HHC
| 1030 | 2012-08-10 04:29 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2012-09-10 15:04 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2012-09-10 15:18 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2012-09-10 15:19 | Weather | Lightning Arrester/Transformer failure | 0 | HHC
| 1030 | 2012-12-01 01:36 | Equipment | Arrester (lightning) failure | 0 | HHC
| 1030 | 2012-12-13 12:02 | Equipment | Transformer faulted/mechanical | 0 | HHC
| 1030 | 2012-12-27 22:53 | Undetermined | Undetermined | 0 | HHC
| 1030 | 2013-03-08 05:54 | Equipment | Insulator/pin failure/wire floating | 0 | HHC
| 1030 | 2013-05-06 05:47 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HHC
| 1030 | 2013-10-12 13:39 | Customer Contact | Vehicle contact | 0 | HHC
| 1030 | 2014-01-21 09:13 | Equipment | Fuse holder/fuse cabinet failed | 0 | HHC
| 1030 | 2014-03-09 12:44 | Equipment | Insulator/pin failure/wire floating | 0 | HHC
| 1030 | 2014-05-14 10:26 | Equipment | Pole broke/rotted/on fire | 0 | HHC
| 1094 | 2009-06-03 09:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OLV
| 1094 | 2009-07-20 14:20 | Equipment | Cutout failure | 0 | OLV
| 1094 | 2010-03-14 19:00 | Tree Contact | Tree fell on line | 0 | OLV
| 1094 | 2010-04-02 09:00 | Equipment | Arrester (lightning) failure | 0 | OLV
| 1094 | 2010-07-14 13:07 | Equipment | Fuse overloaded/inadequate fuse size | 1 | OLV
| 1094 | 2010-09-27 12:51 | Equipment | Switch faulted/mechanical | 0 | OLV
| 1094 | 2011-02-20 01:46 | Weather | Wind - wires slap/pole down | 0 | OLV
| 1100 | 2005-09-20 02:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB
| 1100 | 2009-05-08 12:47 | Customer Contact | Vehicle contact | 0 | WRB
| 1100 | 2011-11-09 16:27 | Equipment | Switch faulted/mechanical | 0 | WRB
| 1100 | 2011-11-12 17:25 | Undetermined | Undetermined | 0 | WRB
| 1100 | 2011-11-18 13:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WRB
| 1100 | 2011-12-06 | Undetermined | Undetermined | 0 | WRB
| 1100 | 2011-12-06 09:38 | Weather | Wind - wires slap/pole down | 0 | WRB
| 1101 | 2007-10-22 01:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB
| 1101 | 2007-10-22 02:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB
| 1166 | 2005-01-18 20:00 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2005-03-15 08:17 | Foreign Object | Bird contact | 0 | LLD
| 1166 | 2005-06-30 06:09 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2005-07-31 06:10 | Foreign Object | Bird contact | 0 | LLD
| 1166 | 2006-04-01 00:13 | Customer Contact | Vehicle contact | 0 | LLD
| 1166 | 2006-08-07 07:29 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2006-08-11 07:33 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2006-12-10 01:23 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD
| 1166 | 2008-02-03 18:15 | Weather | Wind - wires slap/pole down | 0 | LLD
| 1166 | 2009-05-13 10:03 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2010-01-22 07:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLD
| 1166 | 2010-09-30 17:39 | Weather | Lightning Arrester/Transformer failure | 0 | LLD
| 1166 | 2010-11-20 13:08 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2010-12-15 14:04 | Foreign Object | Bird contact | 0 | LLD
| 1166 | 2011-01-30 15:36 | Undetermined | Undetermined | 0 | LLD
| 1166 | 2011-04-30 23:13 | Equipment | Pole broke/rotted/on fire | 0 | LLD
| 1166 | 2012-02-15 17:57 | Foreign Object | Flashover/vegetation | 0 | LLD
| 1166 | 2012-07-21 16:36 | Equipment | Crossarm failure | 0 | LLD
| 1166 | 2012-10-26 06:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLD
| 1166 | 2014-02-28 22:16 | Weather | Lightning Arrester/Transformer failure | 0 | LLD
| 1166 | 2014-04-26 02:34 | Foreign Object | Foreign object in distribution line | 0 | LLD
| 1166 | 2014-11-01 04:56 | Undetermined | Undetermined | 0 | LLD
| 1215 | 2006-03-11 07:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD
| 1215 | 2006-03-12 07:14 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2006-08-10 13:34 | Weather | Lightning Arrester/Transformer failure | 0 | CWD
| 1215 | 2007-01-06 03:45 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2007-01-12 02:39 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2007-02-28 23:42 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2007-10-22 09:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD
| 1215 | 2007-12-22 07:43 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CWD
| 1215 | 2008-01-05 07:41 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2008-01-13 02:56 | Equipment | Crossarm failure | 0 | CWD
| 1215 | 2008-03-16 06:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD
| 1215 | 2008-07-15 17:34 | Foreign Object | Bird contact | 1 | CWD
| 1215 | 2008-07-17 14:39 | Foreign Object | Bird contact | 0 | CWD
| 1215 | 2008-07-19 17:24 | Foreign Object | Bird contact | 0 | CWD
| 1215 | 2008-12-17 10:08 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2008-12-18 01:20 | Weather | Ice or snow/Equipment failure | 0 | CWD
| 1215 | 2010-01-15 09:05 | Weather | Ice or snow/Equipment failure | 0 | CWD
| 1215 | 2010-09-07 15:46 | Equipment | Arrester (lightning) failure | 0 | CWD
| 1215 | 2010-09-29 15:09 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2010-10-03 04:59 | Weather | Lightning Arrester/Transformer failure | 0 | CWD
| 1215 | 2011-02-20 01:39 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2011-02-20 05:55 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2011-07-05 17:41 | Undetermined | Undetermined | 1 | CWD
| 1215 | 2011-07-31 12:47 | Weather | Lightning Arrester/Transformer failure | 0 | CWD
| 1215 | 2011-07-31 13:07 | Weather | Lightning Arrester/Transformer failure | 0 | CWD
| 1215 | 2011-08-05 23:20 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2011-11-11 13:08 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2012-01-25 10:15 | Equipment | Pole broke/rotted/on fire | 0 | CWD
| 1215 | 2012-03-17 21:17 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2012-03-18 14:19 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2012-03-18 16:19 | Weather | Ice or snow/Equipment failure | 0 | CWD
| 1215 | 2012-03-18 22:41 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2012-03-24 21:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD
| 1215 | 2012-04-14 04:11 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2012-08-01 09:44 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2012-11-08 09:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CWD
| 1215 | 2013-09-05 12:54 | Weather | Lightning Arrester/Transformer failure | 0 | CWD
| 1215 | 2013-09-05 15:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD
| 1215 | 2013-11-24 17:11 | Foreign Object | Bird contact | 0 | CWD
| 1215 | 2013-11-27 19:51 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2013-12-07 08:02 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2014-04-30 07:45 | Weather | Wind - wires slap/pole down | 0 | CWD
| 1215 | 2014-05-01 06:55 | Equipment | Conductor contact/wire slap | 0 | CWD
| 1215 | 2014-11-18 06:42 | Undetermined | Undetermined | 0 | CWD
| 1215 | 2015-02-05 05:49 | Equipment | Conductor failure/wire down | 0 | CWD
| 1233 | 2005-02-24 19:00 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2005-02-24 19:40 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2005-02-26 00:43 | Equipment | Fuse overloaded/inadequate fuse size | 0 | RBH
| 1233 | 2005-04-18 08:13 | Foreign Object | Bird contact | 0 | RBH
| 1233 | 2005-09-20 02:23 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2005-09-20 11:40 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2005-09-21 02:39 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2008-03-05 23:32 | Foreign Object | Foreign object in distribution line | 0 | RBH
| 1233 | 2008-06-22 09:21 | Foreign Object | Foreign object in distribution line | 0 | RBH
| 1233 | 2009-04-13 17:10 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBH
| 1233 | 2009-06-10 07:20 | Foreign Object | Bird contact | 0 | RBH
| 1233 | 2009-09-29 08:15 | Foreign Object | Foreign object in distribution line | 0 | RBH
| 1233 | 2009-10-26 11:26 | Equipment | Arrester (lightning) failure | 0 | RBH
| 1233 | 2010-01-21 13:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBH
| 1233 | 2010-10-20 15:50 | Equipment | Transformer faulted/mechanical | 0 | RBH
| 1233 | 2011-11-01 13:01 | Customer Contact | Vehicle contact | 0 | RBH
| 1233 | 2013-01-30 17:00 | Undetermined | Undetermined | 0 | RBH
| 1233 | 2013-06-17 11:03 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBH
| 1233 | 2013-10-09 23:20 | Undetermined | Undetermined | 0 | RBH
| 1233 | 2013-10-28 02:27 | Equipment | Arrester (lightning) failure | 0 | RBH
| 1233 | 2013-10-28 21:01 | Equipment | Arrester (lightning) failure | 0 | RBH
| 1233 | 2014-02-28 14:39 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2014-02-28 15:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBH
| 1233 | 2014-03-02 11:43 | Undetermined | Undetermined | 0 | RBH
| 1233 | 2014-08-29 10:52 | Customer Contact | Vehicle contact | 0 | RBH
| 1233 | 2014-09-16 15:45 | Weather | Lightning Arrester/Transformer failure | 0 | RBH
| 1233 | 2014-12-18 19:18 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBH
| 1234 | 2011-11-02 11:04 | Customer Contact | Heavy equp contact/digin | 0 | FBK
| 1234 | 2012-05-23 11:23 | Customer Contact | Heavy equp contact/digin | 0 | FBK
| 1234 | 2012-12-30 13:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 1234 | 2013-05-02 13:14 | Weather | Wind - wires slap/pole down | 0 | FBK
| 1234 | 2013-11-01 11:33 | Undetermined | Undetermined | 0 | FBK
| 1234 | 2014-03-10 08:14 | Undetermined | Undetermined | 0 | FBK
| 1234 | 2014-11-01 09:30 | Equipment | Transformer faulted/mechanical | 0 | FBK
| 1234 | 2015-01-20 17:15 | Equipment | Cutout failure | 0 | FBK
| 1250 | 2005-01-20 11:02 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2005-01-20 11:12 | Equipment | Conductor failure/wire down | 0 | RSF
| 1250 | 2005-05-01 07:31 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2005-09-06 16:46 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RSF
| 1250 | 2006-04-10 01:30 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2007-08-26 07:32 | Weather | Lightning Arrester/Transformer failure | 0 | RSF
| 1250 | 2007-12-27 08:30 | Customer Contact | Heavy equp contact/digin | 0 | RSF
| 1250 | 2008-03-27 11:21 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2008-03-27 18:31 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2008-05-28 02:53 | Foreign Object | Foreign object in distribution line | 0 | RSF
| 1250 | 2008-09-14 11:56 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RSF
| 1250 | 2008-09-18 15:59 | Foreign Object | Foreign object in distribution line | 0 | RSF
| 1250 | 2009-06-03 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 1250 | 2010-01-21 23:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 1250 | 2011-03-28 15:50 | Equipment | Fuse holder/fuse cabinet failed | 0 | RSF
| 1250 | 2011-11-09 02:45 | Foreign Object | Bird contact | 0 | RSF
| 1250 | 2012-08-07 09:54 | Equipment | Crossarm failure | 0 | RSF
| 1250 | 2012-12-31 18:08 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2013-05-31 16:41 | Undetermined | Undetermined | 0 | RSF
| 1250 | 2014-07-17 06:18 | Customer Contact | Vehicle contact | 0 | RSF
| 1458 | 2005-07-23 09:42 | Weather | Lightning Arrester/Transformer failure | 0 | ANE
| 1458 | 2005-08-28 16:13 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ANE
| 1458 | 2005-09-20 10:11 | Weather | Lightning Arrester/Transformer failure | 0 | ANE
| 1458 | 2006-07-15 14:35 | Weather | Lightning Arrester/Transformer failure | 1 | ANE
| 1458 | 2006-07-21 18:35 | Undetermined | Undetermined | 0 | ANE
| 1458 | 2006-07-22 13:02 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ANE
| 1458 | 2007-03-21 01:10 | Undetermined | Undetermined | 0 | ANE
| 1458 | 2007-03-21 09:37 | Customer Contact | Vehicle contact | 0 | ANE
| 1458 | 2007-09-12 11:06 | Tree Contact | Palm tree contact | 0 | ANE
| 1458 | 2007-10-22 11:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 1458 | 2007-10-23 08:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 1458 | 2008-02-14 14:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 1458 | 2009-01-11 02:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 1458 | 2009-11-28 18:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 1458 | 2010-09-30 17:41 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 1458 | 2011-05-08 23:32 | Undetermined | Undetermined | 0 | ANE
| 1458 | 2011-11-16 05:57 | Equipment | Cutout failure | 0 | ANE
| 1458 | 2012-05-24 06:03 | Equipment | Capacitor failure | 0 | ANE
| 1458 | 2012-05-26 09:19 | Foreign Object | Bird contact | 0 | ANE
| 1458 | 2012-06-02 16:16 | Undetermined | Undetermined | 0 | ANE
| 1458 | 2013-02-16 09:23 | Undetermined | Undetermined | 0 | ANE
| 1458 | 2013-07-20 20:25 | Customer Contact | Vehicle contact | 0 | ANE
| 1458 | 2013-08-04 16:16 | Equipment | Fuse holder/fuse cabinet failed | 0 | ANE
| 1458 | 2013-09-16 13:35 | Foreign Object | Bird contact | 0 | ANE
| 1458 | 2014-05-08 22:50 | Customer Contact | Vehicle contact | 0 | ANE
| 157 | 2005-03-31 13:21 | Weather | Circuit Flashover/fog/foreign object | 0 | BAJC1
| 157 | 2005-07-06 07:52 | Undetermined | Undetermined | 1 | BAJC1
| 157 | 2005-07-23 13:12 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2005-08-08 08:18 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2005-11-14 15:58 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2005-11-16 17:33 | Customer Contact | Heavy equp contact/digin | 0 | BAJC1
| 157 | 2005-12-20 22:31 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2005-12-23 07:04 | Equipment | Cutout failure | 0 | BAJC1
| 157 | 2006-01-05 18:13 | Foreign Object | Animal contact | 0 | BAJC1
| 157 | 2006-02-26 11:04 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2006-03-09 16:20 | Foreign Object | Foreign object in distribution line | 0 | BAJC1
| 157 | 2006-05-22 03:53 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2006-07-19 11:44 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2006-08-23 08:25 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BAJC1
| 157 | 2006-09-03 11:27 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2006-09-03 12:53 | Weather | Wind - wires slap/pole down | 0 | BAJC1
| 157 | 2006-10-13 05:00 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2006-10-14 02:27 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2006-10-14 07:12 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2006-10-27 10:56 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2006-12-16 11:43 | Foreign Object | Damage by gunshot | 0 | BAJC1
| 157 | 2006-12-27 15:15 | Weather | Tree fell on line due to storm/wind | 0 | BAJC1
| 157 | 2007-02-13 15:17 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2007-03-03 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2007-03-29 14:20 | Equipment | Arrester (lightning) failure | 0 | BAJC1
| 157 | 2007-07-10 14:07 | Equipment | Conductor failure/wire down | 1 | BAJC1
| 157 | 2007-10-21 09:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2007-12-06 15:53 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2008-01-27 04:20 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2008-01-27 11:02 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2008-02-14 19:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2008-03-30 08:21 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2008-04-08 04:24 | Equipment | Crossarm failure | 0 | BAJC1
| 157 | 2008-04-24 06:54 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2008-05-06 05:44 | Equipment | Insulator/pin failure/wire floating | 0 | BAJC1
| 157 | 2008-09-21 05:45 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2008-10-21 17:19 | Equipment | Transformer faulted/mechanical | 0 | BAJC1
| 157 | 2008-11-08 10:55 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2008-11-25 10:59 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2009-06-02 13:53 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2009-08-29 08:37 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2009-09-01 12:40 | Equipment | Regulator faulted/mechanical | 0 | BAJC1
| 157 | 2009-09-01 14:57 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2009-09-01 15:27 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2009-09-24 23:23 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2009-10-18 14:19 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2009-10-29 23:12 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2009-11-13 06:51 | Equipment | Pole broke/rotted/on fire | 0 | BAJC1
| 157 | 2009-12-01 14:55 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2009-12-07 16:25 | Weather | Wind - wires slap/pole down | 0 | BAJC1
| 157 | 2009-12-07 17:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2009-12-23 03:44 | Weather | Wind - wires slap/pole down | 0 | BAJC1
| 157 | 2010-02-27 17:13 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2010-05-23 21:52 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2010-05-31 10:24 | Foreign Object | Foreign object in distribution line | 0 | BAJC1
| 157 | 2010-06-02 14:56 | Equipment | Transformer faulted/mechanical | 0 | BAJC1
| 157 | 2010-07-03 11:38 | Undetermined | Undetermined | 1 | BAJC1
| 157 | 2010-08-02 12:18 | Tree Contact | Tree fell on line | 0 | BAJC1
| 157 | 2010-08-02 21:42 | Tree Contact | Tree fell on line | 0 | BAJC1
| 157 | 2010-08-07 15:10 | Equipment | Fuse holder/fuse cabinet failed | 0 | BAJC1
| 157 | 2010-08-22 05:41 | Equipment | Conductor failure/wire down | 0 | BAJC1
| 157 | 2010-09-30 14:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2010-10-20 01:08 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2010-11-03 10:44 | Weather | Tree fell on line due to storm/wind | 0 | BAJC1
| 157 | 2011-02-05 13:50 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2011-04-06 10:42 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2011-05-08 22:48 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2011-05-15 12:02 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2011-05-16 09:41 | Equipment | Conductor failure/wire down | 0 | BAJC1
| 157 | 2011-06-17 09:50 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2011-07-01 21:25 | Equipment | Transformer faulted/mechanical | 0 | BAJC1
| 157 | 2011-08-28 05:04 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2011-09-23 16:29 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2011-11-10 09:42 | Equipment | Recloser/breaker faulted/mechanical | 0 | BAJC1
| 157 | 2011-11-13 09:30 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2011-12-12 21:06 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2012-02-15 23:01 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2012-02-16 11:41 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2012-02-16 17:59 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2012-02-20 13:32 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2012-05-12 09:04 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2012-05-16 23:03 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2012-05-30 14:45 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2012-06-03 19:32 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2012-07-09 18:22 | Undetermined | Undetermined | 1 | BAJC1
| 157 | 2012-08-01 15:03 | Foreign Object | Bird contact | 0 | BAJC1
| 157 | 2012-08-16 13:37 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2012-08-30 13:44 | Customer Contact | Vehicle contact | 0 | BAJC1
| 157 | 2012-09-10 15:59 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2012-10-12 07:07 | Equipment | Arrester (lightning) failure | 0 | BAJC1
| 157 | 2012-12-30 13:37 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2013-09-27 06:25 | Undetermined | Undetermined | 0 | BAJC1
| 157 | 2014-01-25 10:13 | Equipment | Arrester (lightning) failure | 0 | BAJC1
| 157 | 2014-04-30 06:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2014-05-13 07:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1
| 157 | 2014-05-13 09:27 | Weather | Wind - wires slap/pole down | 0 | BAJC1
| 157 | 2014-06-15 09:56 | Customer Contact | Heavy equp contact/digin | 0 | BAJC1
| 157 | 2014-08-03 13:13 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2014-08-03 13:13 | Weather | Lightning Arrester/Transformer failure | 0 | BAJC1
| 157 | 2015-01-09 16:05 | Equipment | Fuse overloaded/inadequate fuse size | 0 | BAJC1
| 157 | 2015-02-18 23:48 | Customer Contact | Vehicle contact | 0 | BAJC1
| 170 | 2005-01-11 14:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 170 | 2005-04-09 01:33 | Weather | Wind - wires slap/pole down | 0 | BRG
| 170 | 2005-04-10 07:16 | Equipment | Conductor failure/wire down | 0 | BRG
| 170 | 2005-08-08 05:05 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 170 | 2005-08-24 09:07 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 170 | 2005-09-15 13:09 | Foreign Object | Foreign object in distribution line | 0 | BRG
| 170 | 2005-10-16 19:30 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 170 | 2005-12-03 13:18 | Equipment | Cutout failure | 0 | BRG
| 170 | 2006-01-16 10:57 | Customer Contact | Vehicle contact | 0 | BRG
| 170 | 2006-03-09 14:30 | Foreign Object | Foreign object in distribution line | 0 | BRG
| 170 | 2006-04-06 06:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 170 | 2006-04-09 11:48 | Foreign Object | Bird contact | 0 | BRG
| 170 | 2006-05-14 05:42 | Undetermined | Undetermined | 0 | BRG
| 170 | 2006-05-29 14:03 | Foreign Object | Vandalism | 0 | BRG
| 170 | 2006-12-24 11:34 | Equipment | Fuse holder/fuse cabinet failed | 0 | BRG
| 170 | 2007-01-05 11:43 | Equipment | Conductor failure/wire down | 0 | BRG
| 170 | 2007-01-27 11:35 | Undetermined | Undetermined | 0 | BRG
| 170 | 2007-03-10 11:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 170 | 2007-06-10 10:53 | Equipment | Fuse overloaded/inadequate fuse size | 0 | BRG
| 170 | 2007-08-26 13:40 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 170 | 2007-12-02 02:16 | Equipment | Conductor failure/wire down | 0 | BRG
| 170 | 2007-12-16 03:34 | Equipment | Conductor failure/wire down | 0 | BRG
| 170 | 2008-01-28 12:51 | Equipment | Cutout failure | 0 | BRG
| 170 | 2008-02-02 14:33 | Equipment | Conductor failure/wire down | 0 | BRG
| 170 | 2008-02-03 13:41 | Weather | Tree fell on line due to storm/wind | 0 | BRG
| 170 | 2008-05-24 09:30 | Undetermined | Undetermined | 0 | BRG
| 170 | 2008-10-04 19:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 170 | 2008-11-28 12:06 | Undetermined | Undetermined | 0 | BRG
| 170 | 2008-12-18 11:44 | Undetermined | Undetermined | 0 | BRG
| 170 | 2008-12-20 12:14 | Undetermined | Undetermined | 0 | BRG
| 170 | 2008-12-22 14:59 | Undetermined | Undetermined | 0 | BRG
| 170 | 2009-03-22 10:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 170 | 2009-03-25 18:42 | Undetermined | Undetermined | 0 | BRG
| 170 | 2009-04-08 09:14 | Customer Contact | Vehicle contact | 0 | BRG
| 170 | 2009-05-03 16:48 | Undetermined | Undetermined | 0 | BRG
| 170 | 2009-11-05 08:11 | Equipment | Pole broke/rotted/on fire | 0 | BRG
| 170 | 2009-12-07 14:44 | Weather | Wind - wires slap/pole down | 0 | BRG
| 170 | 2010-01-22 07:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 170 | 2010-04-04 15:42 | Weather | Earthquake | 0 | BRG
| 170 | 2010-05-18 09:13 | Customer Contact | Vehicle contact | 0 | BRG
| 170 | 2010-07-15 16:43 | Weather | Lightning Arrester/Transformer failure | 1 | BRG
| 170 | 2010-07-16 12:59 | Undetermined | Undetermined | 0 | BRG
| 170 | 2010-07-16 16:07 | Undetermined | Undetermined | 0 | BRG
| 170 | 2010-10-03 14:53 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 170 | 2011-07-07 15:21 | Weather | Lightning Arrester/Transformer failure | 1 | BRG
| 170 | 2011-07-07 15:49 | Weather | Lightning Arrester/Transformer failure | 1 | BRG
| 170 | 2011-07-08 02:03 | Weather | Lightning Arrester/Transformer failure | 1 | BRG
| 170 | 2011-09-05 13:58 | Undetermined | Undetermined | 0 | BRG
| 170 | 2011-09-05 22:37 | Undetermined | Undetermined | 0 | BRG
| 170 | 2012-01-21 14:27 | Weather | Wind - wires slap/pole down | 0 | BRG
| 170 | 2012-01-23 07:53 | Tree Contact | Tree fell on line | 0 | BRG
| 170 | 2012-12-15 20:28 | Equipment | Cutout failure | 0 | BRG
| 170 | 2013-02-13 08:19 | Equipment | Capacitor failure | 0 | BRG
| 170 | 2014-03-01 02:00 | Undetermined | Undetermined | 0 | BRG
| 170 | 2015-01-01 21:30 | Equipment | Conductor failure/wire down | 0 | BRG
| 172 | 2005-07-23 03:01 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2005-08-09 18:59 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2005-10-17 06:35 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2006-05-10 23:12 | Undetermined | Undetermined | 0 | BRG
| 172 | 2006-05-23 01:43 | Undetermined | Undetermined | 0 | BRG
| 172 | 2006-06-28 01:54 | Undetermined | Undetermined | 0 | BRG
| 172 | 2007-05-30 05:30 | Undetermined | Undetermined | 0 | BRG
| 172 | 2007-08-26 15:19 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2008-01-23 10:15 | Foreign Object | Bird contact | 0 | BRG
| 172 | 2008-02-03 12:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2008-02-03 17:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2008-05-21 10:13 | Undetermined | Undetermined | 0 | BRG
| 172 | 2008-06-04 14:16 | Weather | Tree fell on line due to storm/wind | 0 | BRG
| 172 | 2008-11-27 06:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BRG
| 172 | 2008-12-05 16:25 | Undetermined | Undetermined | 0 | BRG
| 172 | 2009-03-22 11:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2009-03-22 16:26 | Undetermined | Undetermined | 0 | BRG
| 172 | 2009-04-14 21:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2009-05-21 23:12 | Foreign Object | Bird contact | 0 | BRG
| 172 | 2009-12-07 22:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2009-12-08 05:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2010-04-11 21:46 | Equipment | Crossarm failure | 0 | BRG
| 172 | 2010-04-28 21:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2010-07-16 11:08 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2010-09-06 05:53 | Undetermined | Undetermined | 0 | BRG
| 172 | 2010-09-30 08:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2010-10-01 14:07 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2010-10-17 05:53 | Foreign Object | Aircraft | 0 | BRG
| 172 | 2010-10-20 04:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2011-03-07 08:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2011-05-23 11:57 | Undetermined | Undetermined | 0 | BRG
| 172 | 2011-07-03 16:04 | Undetermined | Undetermined | 1 | BRG
| 172 | 2011-07-07 14:54 | Weather | Lightning Arrester/Transformer failure | 1 | BRG
| 172 | 2011-09-17 07:12 | Foreign Object | Bird contact | 0 | BRG
| 172 | 2011-09-17 18:17 | Foreign Object | Bird contact | 0 | BRG
| 172 | 2011-12-12 10:47 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2011-12-13 13:30 | Undetermined | Undetermined | 0 | BRG
| 172 | 2012-01-21 12:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2012-01-21 13:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2012-01-21 14:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2012-01-21 14:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2012-01-21 14:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG
| 172 | 2012-01-21 14:21 | Weather | Wind - wires slap/pole down | 0 | BRG
| 172 | 2012-03-06 20:48 | Undetermined | Undetermined | 0 | BRG
| 172 | 2012-09-09 20:29 | Weather | Wind - wires slap/pole down | 0 | BRG
| 172 | 2013-02-21 15:35 | Undetermined | Undetermined | 0 | BRG
| 172 | 2013-04-08 08:14 | Weather | Wind - wires slap/pole down | 0 | BRG
| 172 | 2013-04-08 09:00 | Weather | Wind - wires slap/pole down | 0 | BRG
| 172 | 2013-04-08 09:05 | Weather | Wind - wires slap/pole down | 0 | BRG
| 172 | 2013-09-07 15:42 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 172 | 2013-12-07 23:38 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BRG
| 172 | 2014-03-30 17:54 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BRG
| 172 | 2014-03-30 19:33 | Undetermined | Undetermined | 0 | BRG
| 172 | 2014-08-21 13:31 | Weather | Lightning Arrester/Transformer failure | 0 | BRG
| 175 | 2005-01-04 13:00 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2005-03-12 19:42 | Foreign Object | Foreign object in distribution line | 0 | ARH
| 175 | 2005-03-19 14:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2005-05-19 20:00 | Equipment | Transformer faulted/mechanical | 0 | ARH
| 175 | 2005-09-14 10:13 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH
| 175 | 2005-09-14 18:23 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH
| 175 | 2005-10-07 02:40 | Customer Contact | Vehicle contact | 0 | ARH
| 175 | 2005-10-29 00:42 | Customer Contact | Vehicle contact | 0 | ARH
| 175 | 2006-05-05 11:28 | Foreign Object | Bird contact | 0 | ARH
| 175 | 2007-03-03 11:34 | Weather | Tree contact due to storm/high wind | 0 | ARH
| 175 | 2007-03-22 18:14 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 175 | 2007-09-02 14:44 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 175 | 2007-11-05 14:07 | Customer Contact | Heavy equp contact/digin | 0 | ARH
| 175 | 2007-11-26 10:30 | Equipment | Conductor contact/wire slap | 0 | ARH
| 175 | 2007-11-28 08:02 | Equipment | Conductor contact/wire slap | 0 | ARH
| 175 | 2007-11-28 08:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2007-11-28 11:45 | Foreign Object | Bird contact | 0 | ARH
| 175 | 2007-12-25 09:08 | Equipment | Conductor contact/wire slap | 0 | ARH
| 175 | 2007-12-31 15:39 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2007-12-31 21:26 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-01-01 07:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2008-01-03 11:30 | Equipment | Conductor contact/wire slap | 0 | ARH
| 175 | 2008-05-16 08:51 | Undetermined | Undetermined | 0 | ARH
| 175 | 2008-05-29 20:41 | Undetermined | Undetermined | 0 | ARH
| 175 | 2008-09-29 07:41 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 175 | 2008-11-15 11:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2008-12-17 09:51 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-12-17 11:10 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-12-17 11:15 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-12-17 11:20 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-12-17 11:25 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-12-17 11:30 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2008-12-17 11:37 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2009-02-02 20:53 | Customer Contact | Vehicle contact | 0 | ARH
| 175 | 2010-01-19 14:31 | Weather | Wind - wires slap/pole down | 0 | ARH
| 175 | 2010-01-19 18:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2010-03-02 05:47 | Undetermined | Undetermined | 0 | ARH
| 175 | 2010-03-02 13:16 | Tree Contact | Tree fell on line | 0 | ARH
| 175 | 2010-03-25 11:59 | Undetermined | Undetermined | 0 | ARH
| 175 | 2010-09-01 10:32 | Undetermined | Undetermined | 0 | ARH
| 175 | 2010-09-30 13:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2010-09-30 17:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2010-10-01 01:56 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 175 | 2011-02-06 06:28 | Undetermined | Undetermined | 0 | ARH
| 175 | 2011-04-12 17:48 | Equipment | Transformer faulted/mechanical | 0 | ARH
| 175 | 2011-07-06 17:02 | Weather | Lightning Arrester/Transformer failure | 1 | ARH
| 175 | 2011-10-22 17:36 | Foreign Object | Bird contact | 0 | ARH
| 175 | 2011-11-03 15:14 | Equipment | Transformer faulted/mechanical | 0 | ARH
| 175 | 2012-01-11 06:51 | Undetermined | Undetermined | 0 | ARH
| 175 | 2012-02-16 15:53 | Equipment | Switch faulted/mechanical | 0 | ARH
| 175 | 2012-05-03 14:57 | Undetermined | Undetermined | 0 | ARH
| 175 | 2012-05-29 09:44 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH
| 175 | 2012-06-21 09:11 | Foreign Object | Bird contact | 0 | ARH
| 175 | 2012-07-07 13:15 | Foreign Object | Foreign object in distribution line | 1 | ARH
| 175 | 2012-07-16 12:26 | Undetermined | Undetermined | 0 | ARH
| 175 | 2013-01-12 16:24 | Undetermined | Undetermined | 0 | ARH
| 175 | 2013-04-21 12:08 | Equipment | Switch faulted/mechanical | 0 | ARH
| 175 | 2013-04-21 13:28 | Equipment | Switch faulted/mechanical | 0 | ARH
| 175 | 2013-05-03 05:43 | Undetermined | Undetermined | 0 | ARH
| 175 | 2013-06-22 16:12 | Foreign Object | Bird contact | 0 | ARH
| 175 | 2014-04-06 08:06 | Undetermined | Undetermined | 0 | ARH
| 175 | 2014-10-16 21:18 | Foreign Object | Foreign object in distribution line | 0 | ARH
| 175 | 2014-11-29 05:19 | Undetermined | Undetermined | 0 | ARH
| 175 | 2014-11-29 23:13 | Undetermined | Undetermined | 0 | ARH
| 175 | 2014-12-12 08:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 175 | 2014-12-26 05:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH
| 175 | 2014-12-30 17:34 | Tree Contact | Tree fell on line | 0 | ARH
| 175 | 2015-03-02 10:45 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 175 | 2015-03-19 23:48 | Customer Contact | Vehicle contact | 0 | ARH
| 176 | 2005-01-04 13:24 | Weather | Wind - wires slap/pole down | 0 | ARH
| 176 | 2005-01-04 21:15 | Weather | Wind - wires slap/pole down | 0 | ARH
| 176 | 2005-01-07 16:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2005-01-07 18:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2005-01-07 23:51 | Weather | Wind - wires slap/pole down | 0 | ARH
| 176 | 2005-01-10 10:51 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH
| 176 | 2005-08-25 15:03 | Equipment | Crossarm failure | 0 | ARH
| 176 | 2005-09-20 10:53 | Weather | Wind - wires slap/pole down | 0 | ARH
| 176 | 2005-12-06 02:47 | Undetermined | Undetermined | 0 | ARH
| 176 | 2006-02-01 12:59 | Foreign Object | Bird contact | 0 | ARH
| 176 | 2006-03-29 08:46 | Equipment | Flashover/equip contam/overload | 0 | ARH
| 176 | 2006-07-15 16:16 | Weather | Circ. Flashover/storm/high winds/undet. | 1 | ARH
| 176 | 2006-07-22 13:19 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ARH
| 176 | 2006-07-30 04:39 | Undetermined | Undetermined | 0 | ARH
| 176 | 2006-09-04 17:33 | Undetermined | Undetermined | 0 | ARH
| 176 | 2007-01-25 04:16 | Equipment | Fuse holder/fuse cabinet failed | 0 | ARH
| 176 | 2007-07-02 15:00 | Equipment | Transformer faulted/mechanical | 1 | ARH
| 176 | 2007-08-03 17:20 | Equipment | Pole broke/rotted/on fire | 0 | ARH
| 176 | 2007-08-13 15:53 | Tree Contact | Tree fell on line | 0 | ARH
| 176 | 2007-09-01 13:08 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ARH
| 176 | 2007-09-01 17:35 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ARH
| 176 | 2007-10-24 23:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2007-10-25 13:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2007-11-04 18:30 | Equipment | Fuse holder/fuse cabinet failed | 0 | ARH
| 176 | 2007-11-30 18:26 | Equipment | Conductor failure/wire down | 0 | ARH
| 176 | 2007-12-02 11:06 | Equipment | Conductor failure/wire down | 0 | ARH
| 176 | 2007-12-17 16:33 | Undetermined | Undetermined | 0 | ARH
| 176 | 2007-12-23 14:41 | Equipment | Fuse holder/fuse cabinet failed | 0 | ARH
| 176 | 2008-01-07 04:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2008-03-25 09:00 | Undetermined | Undetermined | 0 | ARH
| 176 | 2008-10-16 12:40 | Undetermined | Undetermined | 0 | ARH
| 176 | 2009-03-31 09:00 | Equipment | Cutout failure | 0 | ARH
| 176 | 2009-08-09 11:50 | Equipment | Fuse holder/fuse cabinet failed | 0 | ARH
| 176 | 2010-01-19 14:26 | Weather | Wind - wires slap/pole down | 0 | ARH
| 176 | 2010-01-20 03:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2010-02-08 04:47 | Undetermined | Undetermined | 0 | ARH
| 176 | 2010-02-08 07:50 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 176 | 2010-09-30 13:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2010-09-30 13:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2010-09-30 13:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH
| 176 | 2011-03-05 19:35 | Equipment | Arrester (lightning) failure | 0 | ARH
| 176 | 2011-08-21 08:39 | Undetermined | Undetermined | 0 | ARH
| 176 | 2011-12-21 09:30 | Equipment | Pole broke/rotted/on fire | 0 | ARH
| 176 | 2012-05-17 03:15 | Customer Contact | Vehicle contact | 0 | ARH
| 176 | 2012-08-22 11:02 | Equipment | Crossarm failure | 0 | ARH
| 176 | 2013-08-06 20:29 | Customer Contact | Vehicle contact | 0 | ARH
| 176 | 2013-10-11 12:02 | Undetermined | Undetermined | 0 | ARH
| 176 | 2014-02-19 17:55 | Undetermined | Undetermined | 0 | ARH
| 176 | 2014-02-28 13:16 | Weather | Lightning Arrester/Transformer failure | 0 | ARH
| 176 | 2014-12-13 03:15 | Equipment | Conductor failure/wire down | 0 | ARH
| 181 | 2005-01-04 07:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ESC
| 181 | 2007-05-28 07:31 | Undetermined | Undetermined | 0 | ESC
| 181 | 2010-08-02 15:56 | Customer Contact | Vehicle contact | 0 | ESC
| 181 | 2011-09-30 23:24 | Undetermined | Undetermined | 0 | ESC
| 204 | 2005-01-11 03:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP
| 204 | 2005-01-11 12:15 | Weather | Flood | 0 | CAP
| 204 | 2005-02-09 13:57 | Foreign Object | Bird contact | 0 | CAP
| 204 | 2005-03-02 23:26 | Customer Contact | Vehicle contact | 0 | CAP
| 204 | 2005-05-12 08:15 | Undetermined | Undetermined | 0 | CAP
| 204 | 2005-06-13 13:52 | Undetermined | Undetermined | 0 | CAP
| 204 | 2005-06-24 19:54 | Undetermined | Undetermined | 0 | CAP
| 204 | 2005-09-28 23:13 | Equipment | Arrester (lightning) failure | 0 | CAP
| 204 | 2005-11-13 08:27 | Undetermined | Undetermined | 0 | CAP
| 204 | 2005-11-14 08:54 | Undetermined | Undetermined | 0 | CAP
| 204 | 2005-12-02 22:47 | Undetermined | Undetermined | 0 | CAP
| 204 | 2005-12-03 06:37 | Tree Contact | Tree fell on line | 0 | CAP
| 204 | 2005-12-04 08:55 | Undetermined | Undetermined | 0 | CAP
| 204 | 2006-01-10 14:48 | Undetermined | Undetermined | 0 | CAP
| 204 | 2006-07-27 10:49 | Undetermined | Undetermined | 0 | CAP
| 204 | 2006-08-03 12:40 | Equipment | Regulator overloaded/electrical | 0 | CAP
| 204 | 2007-01-05 12:23 | Customer Contact | Vehicle contact | 0 | CAP
| 204 | 2007-01-31 11:33 | Undetermined | Undetermined | 0 | CAP
| 204 | 2007-04-23 09:20 | Equipment | Cutout failure | 0 | CAP
| 204 | 2007-08-26 10:14 | Weather | Lightning Arrester/Transformer failure | 0 | CAP
| 204 | 2008-08-17 11:32 | Foreign Object | Animal contact | 0 | CAP
| 204 | 2009-05-11 08:35 | Foreign Object | Foreign object in distribution line | 0 | CAP
| 204 | 2009-06-03 08:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP
| 204 | 2009-06-03 09:01 | Weather | Lightning Arrester/Transformer failure | 0 | CAP
| 204 | 2009-09-09 10:38 | Undetermined | Undetermined | 0 | CAP
| 204 | 2010-08-22 00:12 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CAP
| 204 | 2010-10-09 12:55 | Foreign Object | Bird contact | 0 | CAP
| 204 | 2010-10-19 12:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP
| 204 | 2013-08-08 19:58 | Foreign Object | Damage by gunshot | 0 | CAP
| 204 | 2013-10-24 05:57 | Undetermined | Undetermined | 0 | CAP
| 206 | 2005-01-07 12:01 | Weather | Tree fell on line due to storm/wind | 0 | CBD
| 206 | 2005-01-11 03:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2005-01-11 03:43 | Weather | Tree fell on line due to storm/wind | 0 | CBD
| 206 | 2005-03-15 15:23 | Customer Contact | Vehicle contact | 0 | CBD
| 206 | 2005-03-28 08:40 | Equipment | Crossarm failure | 0 | CBD
| 206 | 2005-05-14 00:46 | Customer Contact | Vehicle contact | 0 | CBD
| 206 | 2005-12-17 02:37 | Customer Contact | Vehicle contact | 0 | CBD
| 206 | 2006-01-02 00:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2006-01-02 10:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2006-01-02 12:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2006-01-02 12:40 | Weather | Palm frond contact due to storm/wind | 0 | CBD
| 206 | 2006-01-02 14:00 | Weather | Wind - wires slap/pole down | 0 | CBD
| 206 | 2006-01-22 19:46 | Customer Contact | Vehicle contact | 0 | CBD
| 206 | 2006-08-24 17:51 | Undetermined | Undetermined | 0 | CBD
| 206 | 2007-03-20 14:03 | Equipment | Transformer faulted/mechanical | 0 | CBD
| 206 | 2007-07-26 14:03 | Equipment | Cutout failure | 0 | CBD
| 206 | 2007-10-22 04:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2008-02-14 18:02 | Tree Contact | Tree fell on line | 0 | CBD
| 206 | 2008-05-24 17:41 | Undetermined | Undetermined | 0 | CBD
| 206 | 2008-09-29 07:40 | Weather | Lightning Arrester/Transformer failure | 0 | CBD
| 206 | 2008-12-09 14:40 | Equipment | Conductor failure/wire down | 0 | CBD
| 206 | 2009-11-22 22:04 | Equipment | Cutout failure | 0 | CBD
| 206 | 2009-12-07 17:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2010-01-20 17:57 | Tree Contact | Tree fell on line | 0 | CBD
| 206 | 2010-01-22 19:42 | Weather | Tree fell on line due to storm/wind | 0 | CBD
| 206 | 2010-01-23 12:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD
| 206 | 2010-03-18 16:30 | Customer Contact | Vehicle contact | 0 | CBD
| 206 | 2010-06-20 10:14 | Equipment | Arrester (lightning) failure | 0 | CBD
| 206 | 2010-06-20 15:12 | Equipment | Arrester (lightning) failure | 0 | CBD
| 206 | 2010-09-01 02:42 | Customer Contact | Vehicle contact | 0 | CBD
| 206 | 2010-11-23 03:21 | Undetermined | Undetermined | 0 | CBD
| 206 | 2010-11-24 06:07 | Undetermined | Undetermined | 0 | CBD
| 206 | 2010-12-20 18:28 | Weather | Tree fell on line due to storm/wind | 0 | CBD
| 206 | 2010-12-30 02:41 | Weather | Tree fell on line due to storm/wind | 0 | CBD
| 206 | 2011-06-22 13:01 | Undetermined | Undetermined | 0 | CBD
| 206 | 2011-10-24 12:52 | Undetermined | Undetermined | 0 | CBD
| 206 | 2012-02-05 07:41 | Foreign Object | Bird contact | 0 | CBD
| 206 | 2012-03-18 17:14 | Foreign Object | Foreign object in distribution line | 0 | CBD
| 206 | 2012-07-04 17:52 | Foreign Object | Foreign object in distribution line | 1 | CBD
| 206 | 2012-11-02 16:45 | Undetermined | Undetermined | 0 | CBD
| 206 | 2012-12-25 10:16 | Undetermined | Undetermined | 0 | CBD
| 206 | 2012-12-25 11:11 | Equipment | Conductor failure/wire down | 0 | CBD
| 206 | 2013-06-06 08:39 | Foreign Object | Foreign object in distribution line | 0 | CBD
| 206 | 2013-10-11 10:05 | Undetermined | Undetermined | 0 | CBD
| 206 | 2014-08-08 12:53 | Foreign Object | Foreign object in distribution line | 0 | CBD
| 210 | 2005-05-12 13:52 | Undetermined | Undetermined | 0 | COY
| 210 | 2005-07-31 17:15 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2005-08-07 12:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY
| 210 | 2005-08-08 15:52 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2005-08-08 18:16 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2005-08-09 08:03 | Weather | Wind - wires slap/pole down | 0 | COY
| 210 | 2005-09-19 23:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY
| 210 | 2005-09-20 05:30 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2005-10-16 20:36 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2006-02-25 07:31 | Undetermined | Undetermined | 0 | COY
| 210 | 2006-06-27 09:27 | Foreign Object | Animal contact | 0 | COY
| 210 | 2006-07-22 21:21 | Weather | Tree contact due to storm/high wind | 0 | COY
| 210 | 2007-06-23 06:24 | Undetermined | Undetermined | 0 | COY
| 210 | 2007-07-20 07:21 | Equipment | Cutout failure | 0 | COY
| 210 | 2007-10-24 17:47 | Undetermined | Undetermined | 0 | COY
| 210 | 2008-08-25 14:44 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2008-11-04 10:55 | Equipment | Cutout failure | 0 | COY
| 210 | 2008-11-28 12:37 | Equipment | Arrester (lightning) failure | 0 | COY
| 210 | 2009-01-10 10:10 | Undetermined | Undetermined | 0 | COY
| 210 | 2010-06-27 13:30 | Undetermined | Undetermined | 0 | COY
| 210 | 2010-08-26 13:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY
| 210 | 2010-09-30 07:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY
| 210 | 2010-10-19 19:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY
| 210 | 2010-11-27 08:17 | Undetermined | Undetermined | 0 | COY
| 210 | 2011-04-13 16:30 | Undetermined | Undetermined | 0 | COY
| 210 | 2011-06-14 09:20 | Equipment | Conductor failure/wire down | 0 | COY
| 210 | 2011-07-30 15:28 | Weather | Tree fell on line due to storm/wind | 0 | COY
| 210 | 2011-07-31 14:09 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2011-08-04 06:17 | Equipment | Conductor failure/wire down | 0 | COY
| 210 | 2011-08-28 13:55 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2012-06-10 19:40 | Equipment | Crossarm failure | 0 | COY
| 210 | 2012-08-11 16:36 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2012-08-13 13:20 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2012-09-23 09:16 | Foreign Object | Bird contact | 0 | COY
| 210 | 2012-12-18 15:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY
| 210 | 2013-02-11 21:08 | Undetermined | Undetermined | 0 | COY
| 210 | 2013-09-02 14:41 | Undetermined | Undetermined | 0 | COY
| 210 | 2013-09-06 13:13 | Weather | Lightning Arrester/Transformer failure | 0 | COY
| 210 | 2013-12-27 00:01 | Undetermined | Undetermined | 0 | COY
| 211 | 2005-03-09 06:54 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2005-03-19 14:16 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2005-04-22 12:18 | Undetermined | Undetermined | 0 | EWN
| 211 | 2005-05-23 11:27 | Undetermined | Undetermined | 0 | EWN
| 211 | 2005-07-30 16:00 | Undetermined | Undetermined | 0 | EWN
| 211 | 2005-07-31 16:37 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2005-08-08 22:24 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2005-08-25 10:41 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2005-10-28 19:13 | Undetermined | Undetermined | 0 | EWN
| 211 | 2005-11-18 18:05 | Undetermined | Undetermined | 0 | EWN
| 211 | 2005-11-26 17:06 | Undetermined | Undetermined | 0 | EWN
| 211 | 2005-12-31 06:47 | Undetermined | Undetermined | 0 | EWN
| 211 | 2006-01-31 06:36 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2006-02-01 06:27 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2006-02-24 15:52 | Customer Contact | Vehicle contact | 0 | EWN
| 211 | 2006-03-11 07:55 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2006-06-20 16:05 | Undetermined | Undetermined | 0 | EWN
| 211 | 2006-07-15 17:03 | Weather | Circ. Flashover/storm/high winds/undet. | 1 | EWN
| 211 | 2006-09-02 15:54 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2006-10-04 15:06 | Equipment | Crossarm failure | 0 | EWN
| 211 | 2006-12-28 08:33 | Undetermined | Undetermined | 0 | EWN
| 211 | 2007-01-12 08:15 | Undetermined | Undetermined | 0 | EWN
| 211 | 2007-01-30 06:58 | Foreign Object | Animal contact | 0 | EWN
| 211 | 2007-04-21 06:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN
| 211 | 2007-06-08 08:51 | Undetermined | Undetermined | 0 | EWN
| 211 | 2007-12-24 08:44 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2008-01-08 07:07 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2008-01-13 07:00 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2008-01-23 06:41 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2008-01-30 07:23 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2008-02-04 01:02 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN
| 211 | 2008-08-29 03:54 | Tree Contact | Tree fell on line | 0 | EWN
| 211 | 2008-09-11 17:04 | Undetermined | Undetermined | 0 | EWN
| 211 | 2008-10-20 01:15 | Undetermined | Undetermined | 0 | EWN
| 211 | 2008-10-24 10:40 | Equipment | Crossarm failure | 0 | EWN
| 211 | 2008-12-17 08:50 | Weather | Tree fell on line due to storm/wind | 0 | EWN
| 211 | 2008-12-29 12:55 | Weather | Tree fell on line due to storm/wind | 0 | EWN
| 211 | 2009-02-12 23:30 | Undetermined | Undetermined | 0 | EWN
| 211 | 2009-09-25 04:23 | Undetermined | Undetermined | 0 | EWN
| 211 | 2010-02-24 19:19 | Undetermined | Undetermined | 0 | EWN
| 211 | 2010-03-15 11:51 | Undetermined | Undetermined | 0 | EWN
| 211 | 2010-07-15 16:48 | Weather | Lightning Arrester/Transformer failure | 1 | EWN
| 211 | 2010-11-16 07:57 | Undetermined | Undetermined | 0 | EWN
| 211 | 2011-02-20 05:13 | Undetermined | Undetermined | 0 | EWN
| 211 | 2011-05-02 12:30 | Weather | Wind - wires slap/pole down | 0 | EWN
| 211 | 2011-05-29 11:47 | Equipment | Crossarm failure | 0 | EWN
| 211 | 2011-09-13 06:03 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2011-09-13 10:38 | Undetermined | Undetermined | 0 | EWN
| 211 | 2012-03-06 08:50 | Foreign Object | Bird contact | 0 | EWN
| 211 | 2012-03-18 01:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN
| 211 | 2012-03-18 09:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN
| 211 | 2012-03-18 10:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN
| 211 | 2012-03-18 10:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN
| 211 | 2012-03-18 12:02 | Weather | Wind - wires slap/pole down | 0 | EWN
| 211 | 2012-04-14 05:49 | Undetermined | Undetermined | 0 | EWN
| 211 | 2012-04-14 06:43 | Undetermined | Undetermined | 0 | EWN
| 211 | 2012-04-14 06:53 | Undetermined | Undetermined | 0 | EWN
| 211 | 2012-04-14 07:03 | Undetermined | Undetermined | 0 | EWN
| 211 | 2012-04-14 07:10 | Undetermined | Undetermined | 0 | EWN
| 211 | 2012-08-11 16:49 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2013-01-14 05:41 | Undetermined | Undetermined | 0 | EWN
| 211 | 2013-03-21 07:33 | Undetermined | Undetermined | 0 | EWN
| 211 | 2013-06-27 09:58 | Equipment | Arrester (lightning) failure | 0 | EWN
| 211 | 2013-09-03 15:18 | Weather | Lightning Arrester/Transformer failure | 0 | EWN
| 211 | 2014-01-30 12:46 | Equipment | Arrester (lightning) failure | 0 | EWN
| 211 | 2014-08-03 19:14 | Foreign Object | Foreign object in distribution line | 0 | EWN
| 211 | 2014-10-22 18:03 | Equipment | Fuse holder/fuse cabinet failed | 0 | EWN
| 212 | 2005-01-20 06:41 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2005-02-20 06:22 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2005-02-25 06:03 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2005-03-08 17:00 | Undetermined | Undetermined | 0 | MGY
| 212 | 2005-03-17 06:25 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2005-03-28 20:47 | Equipment | Cutout failure | 0 | MGY
| 212 | 2005-08-10 10:35 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2005-08-10 11:00 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2005-12-22 06:30 | Undetermined | Undetermined | 0 | MGY
| 212 | 2006-01-01 06:37 | Undetermined | Undetermined | 0 | MGY
| 212 | 2006-01-03 06:32 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2006-02-10 11:16 | Undetermined | Undetermined | 0 | MGY
| 212 | 2006-02-28 06:14 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2006-03-21 08:10 | Undetermined | Undetermined | 0 | MGY
| 212 | 2006-05-06 06:45 | Undetermined | Undetermined | 0 | MGY
| 212 | 2006-06-06 17:22 | Undetermined | Undetermined | 0 | MGY
| 212 | 2006-06-13 11:03 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2006-06-23 09:08 | Foreign Object | Animal contact | 0 | MGY
| 212 | 2006-06-26 06:29 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2006-12-28 06:30 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2007-02-18 16:55 | Undetermined | Undetermined | 0 | MGY
| 212 | 2007-04-15 06:12 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2007-08-01 15:19 | Undetermined | Undetermined | 0 | MGY
| 212 | 2007-08-25 17:38 | Undetermined | Undetermined | 0 | MGY
| 212 | 2007-08-31 13:08 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2007-09-01 13:00 | Equipment | Fuse overloaded/inadequate fuse size | 0 | MGY
| 212 | 2007-10-13 09:06 | Undetermined | Undetermined | 0 | MGY
| 212 | 2007-11-30 05:42 | Equipment | Crossarm failure | 0 | MGY
| 212 | 2008-01-05 07:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2008-01-05 13:31 | Equipment | Pole broke/rotted/on fire | 0 | MGY
| 212 | 2008-01-06 06:53 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2008-01-22 06:37 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2008-01-28 06:37 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2008-04-07 06:14 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-05-22 12:59 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2008-06-07 09:30 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-06-17 12:56 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-06-20 12:08 | Equipment | Conductor failure/wire down | 0 | MGY
| 212 | 2008-07-15 08:46 | Undetermined | Undetermined | 1 | MGY
| 212 | 2008-07-16 03:47 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-07-20 06:05 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-07-25 11:27 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-09-01 11:16 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-09-11 17:34 | Undetermined | Undetermined | 0 | MGY
| 212 | 2008-09-14 14:33 | Undetermined | Undetermined | 0 | MGY
| 212 | 2009-05-07 16:39 | Undetermined | Undetermined | 0 | MGY
| 212 | 2009-05-19 15:10 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGY
| 212 | 2009-07-05 06:17 | Foreign Object | Bird contact | 1 | MGY
| 212 | 2009-11-18 08:41 | Undetermined | Undetermined | 0 | MGY
| 212 | 2009-11-30 08:02 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2009-12-07 20:14 | Weather | Wind - wires slap/pole down | 0 | MGY
| 212 | 2009-12-30 06:42 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2010-01-31 08:04 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-03-02 03:21 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-04-05 08:59 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-05-16 15:45 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-07-15 17:37 | Weather | Lightning Arrester/Transformer failure | 1 | MGY
| 212 | 2010-08-16 09:31 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2010-08-26 11:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2010-09-10 18:50 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-10-01 14:58 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2010-10-24 22:52 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-11-15 12:52 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-12-08 06:13 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-12-14 09:33 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-12-17 16:11 | Undetermined | Undetermined | 0 | MGY
| 212 | 2010-12-20 13:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2011-01-05 07:38 | Equipment | Recloser/breaker overloaded/electrical | 0 | MGY
| 212 | 2011-01-15 07:25 | Undetermined | Undetermined | 0 | MGY
| 212 | 2011-01-20 13:02 | Undetermined | Undetermined | 0 | MGY
| 212 | 2011-01-31 06:26 | Undetermined | Undetermined | 0 | MGY
| 212 | 2011-02-08 06:19 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2011-02-15 06:11 | Undetermined | Undetermined | 0 | MGY
| 212 | 2011-02-26 08:24 | Weather | Wind - wires slap/pole down | 0 | MGY
| 212 | 2011-03-11 05:40 | Undetermined | Undetermined | 0 | MGY
| 212 | 2011-07-06 13:08 | Weather | Lightning Arrester/Transformer failure | 1 | MGY
| 212 | 2011-07-30 15:39 | Undetermined | Undetermined | 0 | MGY
| 212 | 2011-08-26 14:45 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2011-08-28 14:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2011-09-15 15:19 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2011-10-16 08:30 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2011-12-16 13:44 | Equipment | Conductor failure/wire down | 0 | MGY
| 212 | 2011-12-18 06:14 | Undetermined | Undetermined | 0 | MGY
| 212 | 2012-02-02 11:33 | Foreign Object | Foreign object in distribution line | 0 | MGY
| 212 | 2012-02-14 06:18 | Undetermined | Undetermined | 0 | MGY
| 212 | 2012-02-27 20:37 | Weather | Wind - wires slap/pole down | 0 | MGY
| 212 | 2012-03-13 06:48 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2012-04-10 03:28 | Undetermined | Undetermined | 0 | MGY
| 212 | 2012-07-06 11:39 | Customer Contact | Vehicle contact | 1 | MGY
| 212 | 2012-08-07 12:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2012-08-09 17:00 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2012-08-22 13:00 | Undetermined | Undetermined | 0 | MGY
| 212 | 2012-08-30 13:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2012-12-18 10:16 | Foreign Object | Bird contact | 0 | MGY
| 212 | 2012-12-24 06:56 | Undetermined | Undetermined | 0 | MGY
| 212 | 2012-12-25 06:34 | Equipment | Conductor failure/wire down | 0 | MGY
| 212 | 2013-02-05 07:53 | Undetermined | Undetermined | 0 | MGY
| 212 | 2013-02-20 05:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2013-03-20 19:25 | Undetermined | Undetermined | 0 | MGY
| 212 | 2013-05-06 07:11 | Equipment | Crossarm failure | 0 | MGY
| 212 | 2013-05-06 13:36 | Equipment | Crossarm failure | 0 | MGY
| 212 | 2013-05-10 05:49 | Undetermined | Undetermined | 0 | MGY
| 212 | 2013-05-16 03:18 | Undetermined | Undetermined | 0 | MGY
| 212 | 2013-05-16 11:29 | Equipment | Crossarm failure | 0 | MGY
| 212 | 2013-06-27 19:30 | Equipment | Fuse overloaded/inadequate fuse size | 0 | MGY
| 212 | 2013-06-28 03:55 | Equipment | Capacitor failure | 0 | MGY
| 212 | 2013-07-22 14:16 | Undetermined | Undetermined | 0 | MGY
| 212 | 2013-09-02 15:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY
| 212 | 2013-09-05 14:15 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2013-09-07 13:16 | Weather | Lightning Arrester/Transformer failure | 0 | MGY
| 212 | 2013-09-28 17:12 | Undetermined | Undetermined | 0 | MGY
| 212 | 2013-11-03 14:30 | Equipment | Fuse holder/fuse cabinet failed | 0 | MGY
| 212 | 2014-02-03 21:36 | Equipment | Conductor contact/wire slap | 0 | MGY
| 212 | 2014-03-30 10:17 | Undetermined | Undetermined | 0 | MGY
| 212 | 2015-01-26 13:56 | Weather | Wind - wires slap/pole down | 0 | MGY
| 214 | 2005-01-03 12:28 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 214 | 2005-01-03 17:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2005-02-02 05:01 | Weather | Tree fell on line due to storm/wind | 0 | RIN
| 214 | 2005-02-02 09:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2005-02-13 05:23 | Customer Contact | Vehicle contact | 0 | RIN
| 214 | 2005-04-20 06:41 | Undetermined | Undetermined | 0 | RIN
| 214 | 2005-06-20 10:09 | Undetermined | Undetermined | 0 | RIN
| 214 | 2005-07-23 02:55 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 214 | 2005-08-20 20:36 | Undetermined | Undetermined | 0 | RIN
| 214 | 2005-12-29 12:50 | Equipment | Conductor failure/wire down | 0 | RIN
| 214 | 2006-03-11 19:38 | Weather | Ice or snow/Equipment failure | 0 | RIN
| 214 | 2006-07-28 10:29 | Undetermined | Undetermined | 0 | RIN
| 214 | 2006-10-05 20:12 | Undetermined | Undetermined | 0 | RIN
| 214 | 2006-10-06 15:39 | Undetermined | Undetermined | 0 | RIN
| 214 | 2007-01-24 12:34 | Undetermined | Undetermined | 0 | RIN
| 214 | 2007-03-04 08:50 | Undetermined | Undetermined | 0 | RIN
| 214 | 2007-06-06 10:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2007-08-07 04:20 | Foreign Object | Bird contact | 0 | RIN
| 214 | 2007-08-15 15:06 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 214 | 2007-08-15 18:58 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 214 | 2007-08-15 20:04 | Undetermined | Undetermined | 0 | RIN
| 214 | 2007-09-01 13:35 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 214 | 2007-09-22 08:42 | Undetermined | Undetermined | 0 | RIN
| 214 | 2007-09-29 20:20 | Undetermined | Undetermined | 0 | RIN
| 214 | 2007-10-22 19:55 | Weather | Tree contact due to storm/high wind | 0 | RIN
| 214 | 2007-11-12 10:36 | Equipment | Recloser/breaker faulted/mechanical | 0 | RIN
| 214 | 2007-11-13 21:16 | Equipment | Recloser/breaker faulted/mechanical | 0 | RIN
| 214 | 2007-11-14 15:22 | Equipment | Recloser/breaker faulted/mechanical | 0 | RIN
| 214 | 2007-11-29 05:27 | Equipment | Recloser/breaker faulted/mechanical | 0 | RIN
| 214 | 2007-11-30 05:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2008-03-30 23:56 | Customer Contact | Vehicle contact | 0 | RIN
| 214 | 2008-12-16 13:38 | Undetermined | Undetermined | 0 | RIN
| 214 | 2008-12-18 02:04 | Weather | Tree fell on line due to storm/wind | 0 | RIN
| 214 | 2009-01-09 23:06 | Weather | Tree fell on line due to storm/wind | 0 | RIN
| 214 | 2009-02-09 06:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2009-02-09 15:28 | Weather | Ice or snow/Equipment failure | 0 | RIN
| 214 | 2009-02-12 13:11 | Weather | Ice or snow/Equipment failure | 0 | RIN
| 214 | 2009-02-25 09:07 | Customer Contact | Vehicle contact | 0 | RIN
| 214 | 2009-03-02 06:27 | Equipment | Arrester (lightning) failure | 0 | RIN
| 214 | 2009-06-07 19:18 | Undetermined | Undetermined | 0 | RIN
| 214 | 2009-07-24 03:31 | Foreign Object | Bird contact | 0 | RIN
| 214 | 2009-12-07 11:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2010-01-12 13:22 | Customer Contact | Line fault/tree trimming | 0 | RIN
| 214 | 2010-01-21 08:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2010-03-24 17:30 | Undetermined | Undetermined | 0 | RIN
| 214 | 2010-06-12 02:35 | Undetermined | Undetermined | 0 | RIN
| 214 | 2010-08-22 19:19 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN
| 214 | 2010-09-27 13:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 214 | 2011-01-23 01:35 | Foreign Object | Foreign object in distribution line | 0 | RIN
| 214 | 2011-01-31 10:40 | Equipment | Conductor contact/wire slap | 0 | RIN
| 214 | 2011-04-07 22:13 | Weather | Ice or snow/Equipment failure | 0 | RIN
| 214 | 2011-07-26 09:01 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 214 | 2012-02-15 16:53 | Undetermined | Undetermined | 0 | RIN
| 214 | 2012-04-28 16:25 | Equipment | Fuse holder/fuse cabinet failed | 0 | RIN
| 214 | 2012-06-11 06:17 | Foreign Object | Bird contact | 0 | RIN
| 214 | 2012-08-03 05:13 | Foreign Object | Bird contact | 0 | RIN
| 214 | 2012-09-10 14:32 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 214 | 2013-01-01 00:08 | Foreign Object | Damage by gunshot | 0 | RIN
| 214 | 2013-04-19 09:44 | Undetermined | Undetermined | 0 | RIN
| 214 | 2014-02-03 15:03 | Foreign Object | Bird contact | 0 | RIN
| 214 | 2014-04-27 15:59 | Customer Contact | Vehicle contact | 0 | RIN
| 214 | 2014-04-28 13:39 | Equipment | Conductor failure/wire down | 0 | RIN
| 214 | 2014-04-30 09:14 | Undetermined | Undetermined | 0 | RIN
| 214 | 2014-05-31 11:23 | Customer Contact | Line fault/tree trimming | 0 | RIN
| 214 | 2014-08-03 16:02 | Undetermined | Undetermined | 0 | RIN
| 214 | 2014-08-04 09:23 | Undetermined | Undetermined | 0 | RIN
| 215 | 2005-02-02 13:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 215 | 2005-02-03 12:03 | Weather | Wind - wires slap/pole down | 0 | RIN
| 215 | 2005-02-24 17:39 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2005-02-25 17:34 | Customer Contact | Vehicle contact | 0 | RIN
| 215 | 2005-03-09 16:36 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 215 | 2005-05-30 10:03 | Equipment | Grd. bank failure | 0 | RIN
| 215 | 2005-07-23 02:38 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2005-09-20 08:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 215 | 2006-01-02 10:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 215 | 2006-01-23 07:16 | Foreign Object | Bird contact | 0 | RIN
| 215 | 2006-04-05 01:16 | Weather | Wind - wires slap/pole down | 0 | RIN
| 215 | 2007-01-08 17:59 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 215 | 2007-08-26 08:22 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2007-10-29 10:48 | Undetermined | Undetermined | 0 | RIN
| 215 | 2008-05-22 19:40 | Undetermined | Undetermined | 0 | RIN
| 215 | 2009-02-20 20:09 | Equipment | Pole broke/rotted/on fire | 0 | RIN
| 215 | 2009-12-07 14:25 | Weather | Tree fell on line due to storm/wind | 0 | RIN
| 215 | 2010-01-19 14:22 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2010-07-07 18:21 | Foreign Object | Bird contact | 1 | RIN
| 215 | 2010-09-10 17:23 | Foreign Object | Bird contact | 0 | RIN
| 215 | 2010-10-19 02:21 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2010-10-19 08:13 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2010-10-19 12:02 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2010-12-20 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 215 | 2010-12-20 18:26 | Weather | Wind - wires slap/pole down | 0 | RIN
| 215 | 2011-05-06 08:19 | Foreign Object | Bird contact | 0 | RIN
| 215 | 2011-05-19 21:55 | Equipment | Arrester (lightning) failure | 0 | RIN
| 215 | 2011-10-02 02:16 | Foreign Object | Foreign object in distribution line | 0 | RIN
| 215 | 2011-10-05 12:36 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2012-09-09 16:52 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 215 | 2013-02-23 13:27 | Undetermined | Undetermined | 0 | RIN
| 215 | 2013-05-16 08:08 | Foreign Object | Bird contact | 0 | RIN
| 215 | 2013-06-03 06:10 | Undetermined | Undetermined | 0 | RIN
| 215 | 2014-02-28 06:48 | Weather | Wind - wires slap/pole down | 0 | RIN
| 215 | 2014-02-28 08:51 | Weather | Wind - wires slap/pole down | 0 | RIN
| 215 | 2014-02-28 15:07 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN
| 215 | 2014-03-18 15:00 | Equipment | Insulator/pin failure/wire floating | 0 | RIN
| 215 | 2014-09-14 11:12 | Weather | Ice or snow/Equipment failure | 0 | RIN
| 215 | 2014-12-03 04:55 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 216 | 2005-04-01 10:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 216 | 2005-07-23 04:52 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 216 | 2005-11-02 14:16 | Undetermined | Undetermined | 0 | RIN
| 216 | 2005-12-11 13:49 | Undetermined | Undetermined | 0 | RIN
| 216 | 2006-01-02 08:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 216 | 2006-01-02 10:48 | Weather | Wind - wires slap/pole down | 0 | RIN
| 216 | 2006-02-05 11:04 | Undetermined | Undetermined | 0 | RIN
| 216 | 2006-02-08 12:21 | Undetermined | Undetermined | 0 | RIN
| 216 | 2006-10-05 03:41 | Customer Contact | Vehicle contact | 0 | RIN
| 216 | 2007-03-04 09:31 | Undetermined | Undetermined | 0 | RIN
| 216 | 2008-04-06 03:39 | Customer Contact | Vehicle contact | 0 | RIN
| 216 | 2008-05-02 06:51 | Equipment | Insulator/pin failure/wire floating | 0 | RIN
| 216 | 2009-01-19 09:08 | Equipment | Cutout failure | 0 | RIN
| 216 | 2010-06-10 08:48 | Customer Contact | Vehicle contact | 0 | RIN
| 216 | 2011-02-26 15:22 | Customer Contact | Vehicle contact | 0 | RIN
| 216 | 2011-05-25 05:35 | Customer Contact | Vehicle contact | 0 | RIN
| 216 | 2012-09-09 17:14 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 216 | 2013-07-25 20:05 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 216 | 2013-12-17 05:26 | Customer Contact | Vehicle contact | 0 | RIN
| 216 | 2014-06-15 15:43 | Foreign Object | Foreign object in distribution line | 0 | RIN
| 217 | 2005-05-03 20:04 | Undetermined | Undetermined | 0 | PAU
| 217 | 2005-05-03 20:04 | Undetermined | Undetermined | 0 | RIN
| 217 | 2005-09-08 12:28 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2005-09-08 12:28 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2005-09-20 06:30 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2005-09-20 06:30 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2005-09-20 07:55 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2005-09-20 07:55 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2005-09-26 07:38 | Equipment | Transformer faulted/mechanical | 0 | PAU
| 217 | 2005-09-26 07:38 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 217 | 2005-10-16 20:22 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2005-10-16 20:22 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2005-12-10 17:37 | Equipment | Regulator faulted/mechanical | 0 | PAU
| 217 | 2005-12-10 17:37 | Equipment | Regulator faulted/mechanical | 0 | RIN
| 217 | 2006-01-23 03:43 | Equipment | Grd. bank failure | 0 | PAU
| 217 | 2006-01-23 03:43 | Equipment | Grd. bank failure | 0 | RIN
| 217 | 2006-01-23 19:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2006-01-23 19:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2006-01-24 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2006-01-24 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2006-04-19 15:58 | Equipment | Transformer faulted/mechanical | 0 | PAU
| 217 | 2006-04-19 15:58 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 217 | 2006-05-05 17:55 | Undetermined | Undetermined | 0 | PAU
| 217 | 2006-05-05 17:55 | Undetermined | Undetermined | 0 | RIN
| 217 | 2006-05-10 06:35 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2006-05-10 06:35 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2006-06-04 04:14 | Undetermined | Undetermined | 0 | PAU
| 217 | 2006-06-04 04:14 | Undetermined | Undetermined | 0 | RIN
| 217 | 2006-06-27 16:20 | Foreign Object | Vandalism | 0 | PAU
| 217 | 2006-06-27 16:20 | Foreign Object | Vandalism | 0 | RIN
| 217 | 2006-09-22 13:45 | Undetermined | Undetermined | 0 | PAU
| 217 | 2006-09-22 13:45 | Undetermined | Undetermined | 0 | RIN
| 217 | 2006-10-16 09:55 | Equipment | Transformer faulted/mechanical | 0 | PAU
| 217 | 2006-10-16 09:55 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 217 | 2006-11-26 16:34 | Undetermined | Undetermined | 0 | PAU
| 217 | 2006-11-26 16:34 | Undetermined | Undetermined | 0 | RIN
| 217 | 2006-12-09 21:48 | Equipment | Cutout failure | 0 | PAU
| 217 | 2006-12-09 21:48 | Equipment | Cutout failure | 0 | RIN
| 217 | 2007-02-22 02:32 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2007-02-22 02:32 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2007-07-05 01:46 | Equipment | Connector/jumper/splice/elbow/rack | 1 | PAU
| 217 | 2007-07-05 01:46 | Equipment | Connector/jumper/splice/elbow/rack | 1 | RIN
| 217 | 2007-07-14 17:32 | Customer Contact | Vehicle contact | 1 | PAU
| 217 | 2007-07-14 17:32 | Customer Contact | Vehicle contact | 1 | RIN
| 217 | 2007-07-29 19:54 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2007-07-29 19:54 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2007-08-13 01:10 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2007-08-13 01:10 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2007-09-11 10:21 | Equipment | Cutout failure | 0 | PAU
| 217 | 2007-09-11 10:21 | Equipment | Cutout failure | 0 | RIN
| 217 | 2007-09-21 03:23 | Equipment | Conductor failure/wire down | 0 | PAU
| 217 | 2007-09-21 03:23 | Equipment | Conductor failure/wire down | 0 | RIN
| 217 | 2007-09-29 18:34 | Equipment | Conductor contact/wire slap | 0 | PAU
| 217 | 2007-09-29 18:34 | Equipment | Conductor contact/wire slap | 0 | RIN
| 217 | 2007-10-01 12:31 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2007-10-01 12:31 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2008-02-20 14:15 | Equipment | Transformer faulted/mechanical | 0 | PAU
| 217 | 2008-02-20 14:15 | Equipment | Transformer faulted/mechanical | 0 | RIN
| 217 | 2008-06-23 07:33 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2008-06-23 07:33 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2008-11-18 19:28 | Undetermined | Undetermined | 0 | PAU
| 217 | 2008-11-18 19:28 | Undetermined | Undetermined | 0 | RIN
| 217 | 2008-12-21 05:51 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2008-12-21 05:51 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2008-12-21 13:31 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2008-12-21 13:31 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2008-12-25 11:12 | Undetermined | Undetermined | 0 | PAU
| 217 | 2008-12-25 11:12 | Undetermined | Undetermined | 0 | RIN
| 217 | 2009-01-24 21:00 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2009-01-24 21:00 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2009-01-25 08:14 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2009-01-25 08:14 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2009-02-04 14:07 | Equipment | Conductor failure/wire down | 0 | PAU
| 217 | 2009-02-04 14:07 | Equipment | Conductor failure/wire down | 0 | RIN
| 217 | 2009-02-11 16:16 | Equipment | Arrester (lightning) failure | 0 | PAU
| 217 | 2009-02-11 16:16 | Equipment | Arrester (lightning) failure | 0 | RIN
| 217 | 2009-06-03 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2009-06-03 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2009-06-03 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2009-06-03 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2009-06-03 16:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2009-06-03 16:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2009-06-03 16:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2009-06-03 16:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2009-06-03 19:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2009-06-03 19:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2009-06-26 10:16 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2009-06-26 10:16 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2009-10-30 22:11 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2009-10-30 22:11 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2009-11-12 13:05 | Equipment | Capacitor failure | 0 | PAU
| 217 | 2009-11-12 13:05 | Equipment | Capacitor failure | 0 | RIN
| 217 | 2009-12-16 09:10 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2009-12-16 09:10 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2010-03-17 09:59 | Foreign Object | Animal contact | 0 | PAU
| 217 | 2010-03-17 09:59 | Foreign Object | Animal contact | 0 | RIN
| 217 | 2010-09-04 14:07 | Equipment | Conductor failure/wire down | 0 | PAU
| 217 | 2010-09-04 14:07 | Equipment | Conductor failure/wire down | 0 | RIN
| 217 | 2010-09-30 21:40 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2010-09-30 21:40 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2010-10-08 13:15 | Customer Contact | Line fault/tree trimming | 0 | PAU
| 217 | 2010-10-08 13:15 | Customer Contact | Line fault/tree trimming | 0 | RIN
| 217 | 2010-10-19 09:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2010-10-19 09:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2010-11-12 18:49 | Equipment | Cutout failure | 0 | PAU
| 217 | 2010-11-12 18:49 | Equipment | Cutout failure | 0 | RIN
| 217 | 2011-01-23 06:44 | Equipment | Conductor failure/wire down | 0 | PAU
| 217 | 2011-01-23 06:44 | Equipment | Conductor failure/wire down | 0 | RIN
| 217 | 2011-01-26 19:31 | Undetermined | Undetermined | 0 | PAU
| 217 | 2011-01-26 19:31 | Undetermined | Undetermined | 0 | RIN
| 217 | 2011-02-19 16:54 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2011-02-19 16:54 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2011-03-02 10:50 | Undetermined | Undetermined | 0 | PAU
| 217 | 2011-03-02 10:50 | Undetermined | Undetermined | 0 | RIN
| 217 | 2011-05-29 05:06 | Undetermined | Undetermined | 0 | PAU
| 217 | 2011-05-29 05:06 | Undetermined | Undetermined | 0 | RIN
| 217 | 2011-06-11 10:30 | Undetermined | Undetermined | 0 | PAU
| 217 | 2011-06-11 10:30 | Undetermined | Undetermined | 0 | RIN
| 217 | 2011-07-03 03:25 | Undetermined | Undetermined | 1 | PAU
| 217 | 2011-07-03 03:25 | Undetermined | Undetermined | 1 | RIN
| 217 | 2011-07-31 06:20 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2011-07-31 06:20 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2011-11-12 18:04 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2011-11-12 18:04 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2012-02-03 11:40 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2012-02-03 11:40 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2012-03-20 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU
| 217 | 2012-03-20 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN
| 217 | 2012-04-18 18:41 | Foreign Object | Bird contact | 0 | PAU
| 217 | 2012-04-18 18:41 | Foreign Object | Bird contact | 0 | RIN
| 217 | 2012-04-19 07:26 | Undetermined | Undetermined | 0 | PAU
| 217 | 2012-04-19 07:26 | Undetermined | Undetermined | 0 | RIN
| 217 | 2012-09-09 17:18 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2012-09-09 17:18 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2012-09-10 15:57 | Weather | Lightning Arrester/Transformer failure | 0 | PAU
| 217 | 2012-09-10 15:57 | Weather | Lightning Arrester/Transformer failure | 0 | RIN
| 217 | 2012-12-13 11:01 | Equipment | Arrester (lightning) failure | 0 | PAU
| 217 | 2012-12-13 11:01 | Equipment | Arrester (lightning) failure | 0 | RIN
| 217 | 2013-01-08 12:01 | Equipment | Cutout failure | 0 | PAU
| 217 | 2013-01-08 12:01 | Equipment | Cutout failure | 0 | RIN
| 217 | 2013-01-13 07:50 | Equipment | Conductor failure/wire down | 0 | PAU
| 217 | 2013-01-13 07:50 | Equipment | Conductor failure/wire down | 0 | RIN
| 217 | 2013-02-23 00:42 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2013-02-23 00:42 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | PAU
| 217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | RIN
| 217 | 2013-12-27 14:35 | Equipment | Pole broke/rotted/on fire | 0 | PAU
| 217 | 2013-12-27 14:35 | Equipment | Pole broke/rotted/on fire | 0 | RIN
| 217 | 2014-02-28 18:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2014-02-28 18:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2014-04-29 16:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU
| 217 | 2014-04-29 16:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN
| 217 | 2014-04-30 08:11 | Undetermined | Undetermined | 0 | PAU
| 217 | 2014-04-30 08:11 | Undetermined | Undetermined | 0 | RIN
| 217 | 2014-04-30 11:21 | Equipment | Conductor failure/wire down | 0 | PAU
| 217 | 2014-04-30 11:21 | Equipment | Conductor failure/wire down | 0 | RIN
| 217 | 2014-05-14 12:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU
| 217 | 2014-05-14 12:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN
| 217 | 2014-07-20 23:53 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2014-07-20 23:53 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2014-07-21 15:54 | Undetermined | Undetermined | 0 | PAU
| 217 | 2014-07-21 15:54 | Undetermined | Undetermined | 0 | RIN
| 217 | 2014-08-08 00:27 | Customer Contact | Vehicle contact | 0 | PAU
| 217 | 2014-08-08 00:27 | Customer Contact | Vehicle contact | 0 | RIN
| 217 | 2014-12-20 12:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU
| 217 | 2014-12-20 12:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN
| 217 | 2015-01-24 04:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU
| 217 | 2015-01-24 04:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN
| 217 | 2015-01-24 07:04 | Equipment | Conductor contact/wire slap | 0 | PAU
| 217 | 2015-01-24 07:04 | Equipment | Conductor contact/wire slap | 0 | RIN
| 217 | 2015-01-24 09:26 | Undetermined | Undetermined | 0 | PAU
| 217 | 2015-01-24 09:26 | Undetermined | Undetermined | 0 | RIN
| 217 | 2015-01-24 14:23 | Equipment | Conductor contact/wire slap | 0 | PAU
| 217 | 2015-01-24 14:23 | Equipment | Conductor contact/wire slap | 0 | RIN
| 220 | 2005-01-10 16:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2005-03-02 10:54 | Undetermined | Undetermined | 0 | YSA
| 220 | 2005-07-04 08:01 | Undetermined | Undetermined | 1 | YSA
| 220 | 2005-07-14 07:43 | Foreign Object | Bird contact | 1 | YSA
| 220 | 2005-07-25 10:00 | Equipment | Pole broke/rotted/on fire | 0 | YSA
| 220 | 2005-07-27 08:05 | Undetermined | Undetermined | 0 | YSA
| 220 | 2005-07-30 13:12 | Undetermined | Undetermined | 0 | YSA
| 220 | 2005-08-11 18:07 | Equipment | Cutout failure | 0 | YSA
| 220 | 2005-09-20 07:51 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 220 | 2005-09-20 08:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2005-09-20 10:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2005-09-23 09:56 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 220 | 2005-09-27 10:20 | Foreign Object | Damage by gunshot | 0 | YSA
| 220 | 2005-10-19 09:53 | Equipment | Arrester (lightning) failure | 0 | YSA
| 220 | 2005-11-10 09:36 | Equipment | Cutout failure | 0 | YSA
| 220 | 2006-03-10 07:52 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 220 | 2006-03-28 23:24 | Weather | Tree fell on line due to storm/wind | 0 | YSA
| 220 | 2006-07-05 18:25 | Undetermined | Undetermined | 1 | YSA
| 220 | 2006-07-18 13:56 | Undetermined | Undetermined | 0 | YSA
| 220 | 2006-08-16 09:40 | Foreign Object | Bird contact | 0 | YSA
| 220 | 2006-11-30 06:19 | Weather | Wind - wires slap/pole down | 0 | YSA
| 220 | 2007-03-30 01:00 | Equipment | Cutout failure | 0 | YSA
| 220 | 2007-06-13 20:00 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA
| 220 | 2007-07-02 12:05 | Undetermined | Undetermined | 1 | YSA
| 220 | 2007-10-22 05:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2008-06-17 10:15 | Undetermined | Undetermined | 0 | YSA
| 220 | 2008-06-24 07:26 | Undetermined | Undetermined | 0 | YSA
| 220 | 2009-05-25 08:18 | Foreign Object | Bird contact | 0 | YSA
| 220 | 2009-09-22 14:17 | Foreign Object | Bird contact | 0 | YSA
| 220 | 2009-11-11 05:49 | Undetermined | Undetermined | 0 | YSA
| 220 | 2010-01-21 07:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2010-01-21 15:59 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 220 | 2010-03-16 02:53 | Undetermined | Undetermined | 0 | YSA
| 220 | 2010-06-13 14:34 | Undetermined | Undetermined | 0 | YSA
| 220 | 2010-07-15 17:57 | Weather | Lightning Arrester/Transformer failure | 1 | YSA
| 220 | 2010-12-10 11:01 | Undetermined | Undetermined | 0 | YSA
| 220 | 2010-12-22 06:44 | Weather | Wind - wires slap/pole down | 0 | YSA
| 220 | 2011-01-25 13:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2011-02-02 06:12 | Weather | Wind - wires slap/pole down | 0 | YSA
| 220 | 2011-02-11 08:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2012-07-09 08:00 | Undetermined | Undetermined | 1 | YSA
| 220 | 2012-08-30 13:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2013-02-27 18:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2013-06-18 19:44 | Undetermined | Undetermined | 0 | YSA
| 220 | 2013-12-09 12:48 | Undetermined | Undetermined | 0 | YSA
| 220 | 2013-12-09 18:05 | Undetermined | Undetermined | 0 | YSA
| 220 | 2014-05-13 06:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 220 | 2014-07-26 12:07 | Undetermined | Undetermined | 0 | YSA
| 220 | 2014-08-03 12:33 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 220 | 2014-11-25 03:41 | Undetermined | Undetermined | 0 | YSA
| 220 | 2015-03-19 08:15 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 221 | 2005-04-01 11:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2005-04-09 00:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2005-04-19 01:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2005-06-03 01:41 | Undetermined | Undetermined | 0 | YSA
| 221 | 2005-08-04 16:16 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2005-08-06 14:46 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2005-08-07 00:14 | Undetermined | Undetermined | 0 | YSA
| 221 | 2005-08-09 18:55 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2005-09-19 23:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2005-10-12 06:47 | Undetermined | Undetermined | 0 | YSA
| 221 | 2005-12-03 09:10 | Undetermined | Undetermined | 0 | YSA
| 221 | 2005-12-24 16:09 | Undetermined | Undetermined | 0 | YSA
| 221 | 2006-01-18 22:43 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2006-01-19 04:38 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2006-02-15 16:08 | Equipment | Conductor failure/wire down | 0 | YSA
| 221 | 2006-03-12 08:48 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2006-03-19 15:19 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2006-07-20 15:06 | Undetermined | Undetermined | 0 | YSA
| 221 | 2006-07-26 16:01 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2006-08-23 13:33 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2006-09-02 16:12 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2006-09-03 15:18 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2006-09-05 18:00 | Customer Contact | Vehicle contact | 0 | YSA
| 221 | 2006-09-21 06:56 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2006-10-22 08:12 | Customer Contact | Vehicle contact | 0 | YSA
| 221 | 2006-10-28 10:45 | Undetermined | Undetermined | 0 | YSA
| 221 | 2006-10-29 14:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2006-11-27 08:38 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2006-11-28 04:23 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2007-02-07 19:10 | Customer Contact | Vehicle contact | 0 | YSA
| 221 | 2007-03-02 13:46 | Equipment | Cutout failure | 0 | YSA
| 221 | 2007-03-15 12:23 | Undetermined | Undetermined | 0 | YSA
| 221 | 2007-06-19 16:38 | Foreign Object | Damage by gunshot | 0 | YSA
| 221 | 2007-10-05 05:07 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2007-10-05 07:40 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2007-10-26 08:39 | Tree Contact | Tree fell on line | 0 | YSA
| 221 | 2007-12-01 06:36 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2007-12-01 07:39 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2008-01-05 04:52 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2008-02-03 12:59 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2008-02-03 13:35 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2008-02-03 17:55 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2008-02-03 18:51 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2008-05-28 06:45 | Undetermined | Undetermined | 0 | YSA
| 221 | 2008-08-04 18:59 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2008-08-16 09:07 | Equipment | Crossarm failure | 0 | YSA
| 221 | 2008-08-25 14:20 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2008-09-17 15:32 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2008-09-19 07:23 | Foreign Object | Bird contact | 0 | YSA
| 221 | 2008-09-22 09:00 | Undetermined | Undetermined | 0 | YSA
| 221 | 2008-12-05 06:38 | Undetermined | Undetermined | 0 | YSA
| 221 | 2008-12-17 09:27 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 221 | 2008-12-18 14:22 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2008-12-19 05:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2008-12-19 06:45 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 221 | 2009-02-09 07:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2009-02-13 14:19 | Undetermined | Undetermined | 0 | YSA
| 221 | 2009-02-16 08:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2009-03-22 12:43 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2009-04-02 13:01 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2009-05-20 16:22 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2009-09-02 13:54 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2009-09-28 06:18 | Undetermined | Undetermined | 0 | YSA
| 221 | 2009-09-30 18:45 | Equipment | Recloser/breaker faulted/mechanical | 0 | YSA
| 221 | 2009-11-13 04:58 | Undetermined | Undetermined | 0 | YSA
| 221 | 2009-12-07 19:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2009-12-07 20:27 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2009-12-07 22:15 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2009-12-08 01:59 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2009-12-22 08:38 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2009-12-22 13:20 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2010-01-18 15:58 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2010-01-18 19:23 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2010-03-09 08:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2010-05-21 15:57 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2010-06-18 18:52 | Undetermined | Undetermined | 0 | YSA
| 221 | 2010-06-18 19:24 | Undetermined | Undetermined | 0 | YSA
| 221 | 2010-07-15 16:02 | Weather | Lightning Arrester/Transformer failure | 1 | YSA
| 221 | 2010-07-20 10:41 | Undetermined | Undetermined | 0 | YSA
| 221 | 2010-08-14 14:31 | Undetermined | Undetermined | 0 | YSA
| 221 | 2010-08-26 18:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2010-09-30 04:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2010-09-30 11:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2010-10-02 16:21 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2010-10-22 02:29 | Customer Contact | Vehicle contact | 0 | YSA
| 221 | 2010-11-16 19:30 | Undetermined | Undetermined | 0 | YSA
| 221 | 2011-01-06 06:22 | Undetermined | Undetermined | 0 | YSA
| 221 | 2011-02-27 10:55 | Equipment | Arrester (lightning) failure | 0 | YSA
| 221 | 2011-05-21 19:04 | Undetermined | Undetermined | 0 | YSA
| 221 | 2011-05-31 19:27 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2011-07-09 05:51 | Undetermined | Undetermined | 1 | YSA
| 221 | 2011-07-13 14:00 | Foreign Object | Bird contact | 1 | YSA
| 221 | 2011-08-28 13:22 | Equipment | Regulator faulted/mechanical | 0 | YSA
| 221 | 2011-09-13 06:07 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2011-10-11 14:54 | Undetermined | Undetermined | 0 | YSA
| 221 | 2011-11-09 08:14 | Foreign Object | Bird contact | 0 | YSA
| 221 | 2012-01-13 04:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2012-01-21 16:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2012-02-13 16:24 | Undetermined | Undetermined | 0 | YSA
| 221 | 2012-02-28 04:37 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 221 | 2012-04-01 03:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2012-04-01 03:23 | Weather | Wind - wires slap/pole down | 0 | YSA
| 221 | 2012-04-13 17:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2012-08-07 12:00 | Undetermined | Undetermined | 0 | YSA
| 221 | 2012-08-11 14:35 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2012-09-04 13:57 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2012-10-12 17:13 | Undetermined | Undetermined | 0 | YSA
| 221 | 2013-07-21 14:20 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2013-08-26 08:37 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2013-09-03 17:14 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 221 | 2013-10-28 09:45 | Equipment | Arrester (lightning) failure | 0 | YSA
| 221 | 2013-12-01 13:31 | Equipment | Pole broke/rotted/on fire | 0 | YSA
| 221 | 2014-02-28 08:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 221 | 2014-02-28 19:30 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 221 | 2014-04-01 04:44 | Foreign Object | Foreign object in distribution line | 0 | YSA
| 221 | 2014-04-07 10:13 | Equipment | Crossarm failure | 0 | YSA
| 221 | 2014-04-07 14:50 | Equipment | Crossarm failure | 0 | YSA
| 221 | 2014-04-13 08:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA
| 221 | 2014-04-14 08:23 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 221 | 2014-06-20 05:29 | Foreign Object | Bird contact | 0 | YSA
| 221 | 2014-06-27 19:47 | Undetermined | Undetermined | 0 | YSA
| 221 | 2015-03-01 23:58 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2005-01-09 06:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2005-02-12 14:01 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-02-25 15:41 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-03-05 17:26 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-03-13 06:29 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-04-01 05:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2005-05-06 00:43 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-05-06 07:36 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2005-05-07 00:16 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2005-05-16 08:18 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-06-08 23:54 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-07-18 19:28 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-07-21 11:48 | Customer Contact | Line fault/tree trimming | 0 | YSA
| 222 | 2005-07-23 05:43 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2005-07-23 07:09 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2005-08-04 07:59 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-08-27 14:47 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2005-08-29 00:09 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2005-09-03 07:01 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2005-09-21 07:20 | Tree Contact | Tree fell on line | 0 | YSA
| 222 | 2005-10-11 13:57 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2005-11-04 15:12 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-11-27 06:06 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-12-01 16:23 | Undetermined | Undetermined | 0 | YSA
| 222 | 2005-12-30 16:47 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-03-10 07:32 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 222 | 2006-03-23 02:55 | Foreign Object | Foreign object in distribution line | 0 | YSA
| 222 | 2006-04-21 14:07 | Equipment | Crossarm failure | 0 | YSA
| 222 | 2006-05-15 18:27 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-05-17 10:39 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-05-20 17:40 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-05-31 08:26 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-06-16 01:45 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2006-07-15 16:22 | Weather | Lightning Arrester/Transformer failure | 1 | YSA
| 222 | 2006-08-15 11:02 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-08-23 13:50 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2006-08-29 13:29 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-10-25 10:31 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2006-11-05 05:50 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-11-29 21:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2006-11-29 22:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2006-11-30 04:49 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-11-30 10:41 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-12-03 09:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA
| 222 | 2006-12-03 11:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2006-12-07 06:49 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-12-26 06:22 | Undetermined | Undetermined | 0 | YSA
| 222 | 2006-12-28 06:26 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-01-04 23:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2007-01-06 02:15 | Weather | Wind - wires slap/pole down | 0 | YSA
| 222 | 2007-01-07 06:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2007-01-07 08:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2007-01-15 06:20 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-01-15 07:08 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-02-12 06:18 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-03-09 09:23 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-03-13 15:04 | Equipment | Crossarm failure | 0 | YSA
| 222 | 2007-03-19 20:28 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-05-27 14:42 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-05-28 15:06 | Equipment | Conductor failure/wire down | 0 | YSA
| 222 | 2007-07-04 07:28 | Equipment | Arrester (lightning) failure | 1 | YSA
| 222 | 2007-07-31 02:10 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-08-09 22:55 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2007-08-15 05:57 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-09-02 14:26 | Tree Contact | Tree fell on line | 0 | YSA
| 222 | 2007-10-09 06:34 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-11-22 06:25 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-12-09 02:15 | Undetermined | Undetermined | 0 | YSA
| 222 | 2007-12-17 10:21 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2007-12-17 19:33 | Undetermined | Undetermined | 0 | YSA
| 222 | 2008-01-07 00:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2008-01-07 03:40 | Weather | Tree fell on line due to storm/wind | 0 | YSA
| 222 | 2008-01-15 06:30 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2008-01-26 06:27 | Undetermined | Undetermined | 0 | YSA
| 222 | 2008-02-03 12:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2008-02-03 23:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2008-02-04 15:18 | Undetermined | Undetermined | 0 | YSA
| 222 | 2008-02-12 15:35 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2008-02-12 17:32 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2008-03-03 05:28 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 222 | 2008-03-06 16:10 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 222 | 2008-03-19 02:07 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2008-05-22 13:38 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2008-05-28 06:43 | Undetermined | Undetermined | 0 | YSA
| 222 | 2008-07-15 18:17 | Undetermined | Undetermined | 1 | YSA
| 222 | 2008-08-07 16:54 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 222 | 2008-08-25 14:36 | Equipment | Regulator overloaded/electrical | 0 | YSA
| 222 | 2008-08-29 10:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2008-09-13 18:44 | Undetermined | Undetermined | 0 | YSA
| 222 | 2008-10-18 06:44 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2008-10-23 15:46 | Weather | Tree fell on line due to storm/wind | 0 | YSA
| 222 | 2008-12-10 21:10 | Equipment | Cutout failure | 0 | YSA
| 222 | 2008-12-17 09:21 | Weather | Tree fell on line due to storm/wind | 0 | YSA
| 222 | 2009-02-05 21:29 | Weather | Wind - wires slap/pole down | 0 | YSA
| 222 | 2009-03-01 14:48 | Undetermined | Undetermined | 0 | YSA
| 222 | 2009-03-22 15:51 | Weather | Tree fell on line due to storm/wind | 0 | YSA
| 222 | 2009-04-08 07:48 | Undetermined | Undetermined | 0 | YSA
| 222 | 2009-05-02 07:32 | Foreign Object | Animal contact | 0 | YSA
| 222 | 2009-10-19 08:24 | Undetermined | Undetermined | 0 | YSA
| 222 | 2009-11-09 16:50 | Undetermined | Undetermined | 0 | YSA
| 222 | 2009-12-10 17:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-01-05 15:36 | Undetermined | Undetermined | 0 | YSA
| 222 | 2010-01-11 06:32 | Undetermined | Undetermined | 0 | YSA
| 222 | 2010-01-19 14:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-01-20 22:05 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2010-01-21 12:39 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 222 | 2010-01-21 13:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-01-22 00:30 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2010-02-05 06:23 | Undetermined | Undetermined | 0 | YSA
| 222 | 2010-04-04 09:34 | Undetermined | Undetermined | 0 | YSA
| 222 | 2010-04-08 07:55 | Foreign Object | Animal contact | 0 | YSA
| 222 | 2010-04-10 07:40 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2010-05-12 12:26 | Foreign Object | Animal contact | 0 | YSA
| 222 | 2010-08-14 14:31 | Undetermined | Undetermined | 0 | YSA
| 222 | 2010-08-23 12:11 | Undetermined | Undetermined | 0 | YSA
| 222 | 2010-09-06 09:50 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 222 | 2010-09-30 07:12 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2010-09-30 09:18 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2010-09-30 11:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-09-30 11:49 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2010-09-30 12:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-09-30 13:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-09-30 19:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-09-30 21:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-10-19 12:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-10-19 13:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA
| 222 | 2010-10-21 20:09 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2011-02-02 07:18 | Weather | Wind - wires slap/pole down | 0 | YSA
| 222 | 2011-02-27 08:27 | Weather | Tree fell on line due to storm/wind | 0 | YSA
| 222 | 2011-04-27 17:00 | Equipment | Crossarm failure | 0 | YSA
| 222 | 2011-08-11 23:18 | Undetermined | Undetermined | 0 | YSA
| 222 | 2011-09-03 09:28 | Foreign Object | Foreign object in distribution line | 0 | YSA
| 222 | 2011-09-23 20:19 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2011-11-10 16:25 | Undetermined | Undetermined | 0 | YSA
| 222 | 2011-12-23 06:26 | Undetermined | Undetermined | 0 | YSA
| 222 | 2012-02-29 06:53 | Undetermined | Undetermined | 0 | YSA
| 222 | 2012-03-01 16:48 | Equipment | Arrester (lightning) failure | 0 | YSA
| 222 | 2012-06-11 15:28 | Foreign Object | Damage by gunshot | 0 | YSA
| 222 | 2012-06-13 15:44 | Equipment | Fuse overloaded/inadequate fuse size | 0 | YSA
| 222 | 2012-06-30 07:50 | Undetermined | Undetermined | 0 | YSA
| 222 | 2012-07-25 18:17 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2012-08-12 13:50 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2012-08-13 08:26 | Undetermined | Undetermined | 0 | YSA
| 222 | 2012-10-09 07:42 | Undetermined | Undetermined | 0 | YSA
| 222 | 2012-10-18 14:20 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-01-10 20:42 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-01-29 06:19 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2013-01-31 13:40 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2013-02-05 06:48 | Equipment | Insulator/pin failure/wire floating | 0 | YSA
| 222 | 2013-02-20 05:08 | Weather | Ice or snow/Equipment failure | 0 | YSA
| 222 | 2013-02-25 15:43 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-03-09 04:51 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-03-13 06:41 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-03-19 08:18 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-05-13 07:30 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2013-09-17 06:30 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-10-08 11:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA
| 222 | 2013-10-30 10:40 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-10-31 10:04 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2013-11-11 02:42 | Customer Contact | Vehicle contact | 0 | YSA
| 222 | 2013-11-11 05:56 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2013-12-06 10:14 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-12-06 14:50 | Undetermined | Undetermined | 0 | YSA
| 222 | 2013-12-13 11:49 | Foreign Object | Bird contact | 0 | YSA
| 222 | 2014-01-09 06:25 | Undetermined | Undetermined | 0 | YSA
| 222 | 2014-01-16 06:24 | Undetermined | Undetermined | 0 | YSA
| 222 | 2014-02-08 09:48 | Undetermined | Undetermined | 0 | YSA
| 222 | 2014-04-26 01:43 | Undetermined | Undetermined | 0 | YSA
| 222 | 2014-07-14 16:15 | Weather | Lightning Arrester/Transformer failure | 1 | YSA
| 222 | 2014-07-29 08:10 | Equipment | Transformer faulted/mechanical | 0 | YSA
| 222 | 2014-08-03 13:56 | Weather | Lightning Arrester/Transformer failure | 0 | YSA
| 222 | 2014-09-04 07:16 | Undetermined | Undetermined | 0 | YSA
| 222 | 2014-10-28 06:34 | Undetermined | Undetermined | 0 | YSA
| 222 | 2014-10-28 19:24 | Equipment | Crossarm failure | 0 | YSA
| 222 | 2014-11-14 09:05 | Equipment | Conductor failure/wire down | 0 | YSA
| 222 | 2014-12-10 07:56 | Undetermined | Undetermined | 0 | YSA
| 222 | 2015-01-05 09:51 | Undetermined | Undetermined | 0 | YSA
| 222 | 2015-01-15 12:38 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA
| 233 | 2005-02-24 19:05 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-02-24 19:05 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-02-25 02:03 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-03-14 14:11 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2005-04-08 20:28 | Undetermined | Undetermined | 0 | FBK
| 233 | 2005-06-07 11:12 | Customer Contact | Heavy equp contact/digin | 0 | FBK
| 233 | 2005-06-09 10:37 | Undetermined | Undetermined | 0 | FBK
| 233 | 2005-06-23 16:50 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2005-08-05 11:27 | Undetermined | Undetermined | 0 | FBK
| 233 | 2005-09-20 01:13 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-09-20 01:14 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-09-20 11:35 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-09-20 15:30 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-09-21 07:20 | Equipment | Fuse overloaded/inadequate fuse size | 0 | FBK
| 233 | 2005-10-15 23:35 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-10-16 16:13 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2005-11-15 10:45 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2005-11-17 16:42 | Equipment | Transformer faulted/mechanical | 0 | FBK
| 233 | 2006-02-18 17:28 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2006-06-10 08:55 | Customer Contact | Heavy equp contact/digin | 0 | FBK
| 233 | 2006-07-28 04:19 | Tree Contact | Tree fell on line | 0 | FBK
| 233 | 2006-08-10 18:32 | Undetermined | Undetermined | 0 | FBK
| 233 | 2006-09-05 10:07 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK
| 233 | 2007-01-27 11:06 | Undetermined | Undetermined | 0 | FBK
| 233 | 2007-02-10 12:36 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2007-03-11 12:45 | Undetermined | Undetermined | 0 | FBK
| 233 | 2007-04-18 09:31 | Tree Contact | Tree fell on line | 0 | FBK
| 233 | 2007-04-26 11:20 | Undetermined | Undetermined | 0 | FBK
| 233 | 2007-07-17 19:13 | Undetermined | Undetermined | 0 | FBK
| 233 | 2007-07-31 03:09 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2007-10-21 14:03 | Weather | Tree contact due to storm/high wind | 0 | FBK
| 233 | 2007-11-25 18:15 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2007-12-24 23:02 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2008-03-06 02:09 | Foreign Object | Vandalism | 0 | FBK
| 233 | 2008-04-11 15:08 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2008-09-19 18:10 | Equipment | Conductor failure/wire down | 0 | FBK
| 233 | 2008-11-27 09:41 | Equipment | Capacitor failure | 0 | FBK
| 233 | 2008-12-01 00:50 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2008-12-15 17:51 | Undetermined | Undetermined | 0 | FBK
| 233 | 2008-12-19 16:59 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2009-01-10 20:26 | Undetermined | Undetermined | 0 | FBK
| 233 | 2009-02-09 15:00 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2009-02-17 04:16 | Weather | Tree fell on line due to storm/wind | 0 | FBK
| 233 | 2009-04-03 10:23 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2009-06-03 12:26 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2009-07-18 05:40 | Undetermined | Undetermined | 0 | FBK
| 233 | 2009-11-28 18:40 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2010-01-02 07:55 | Equipment | Conductor failure/wire down | 0 | FBK
| 233 | 2010-01-09 14:33 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2010-01-19 00:05 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2010-03-16 11:25 | Tree Contact | Tree fell on line | 0 | FBK
| 233 | 2010-04-07 14:37 | Equipment | Transformer faulted/mechanical | 0 | FBK
| 233 | 2010-06-28 16:45 | Equipment | Conductor failure/wire down | 0 | FBK
| 233 | 2010-07-20 06:22 | Undetermined | Undetermined | 0 | FBK
| 233 | 2010-10-19 03:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 233 | 2010-12-21 09:39 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2011-03-05 11:18 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2011-07-25 05:50 | Undetermined | Undetermined | 0 | FBK
| 233 | 2011-09-05 04:52 | Undetermined | Undetermined | 0 | FBK
| 233 | 2011-09-12 18:39 | Undetermined | Undetermined | 0 | FBK
| 233 | 2011-10-10 18:04 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2012-06-12 16:13 | Undetermined | Undetermined | 0 | FBK
| 233 | 2012-08-06 17:55 | Undetermined | Undetermined | 0 | FBK
| 233 | 2012-08-18 17:03 | Undetermined | Undetermined | 0 | FBK
| 233 | 2012-09-10 05:57 | Foreign Object | Bird contact | 0 | FBK
| 233 | 2013-01-10 14:05 | Undetermined | Undetermined | 0 | FBK
| 233 | 2013-02-19 23:09 | Undetermined | Undetermined | 0 | FBK
| 233 | 2013-04-02 21:39 | Equipment | Fuse holder/fuse cabinet failed | 0 | FBK
| 233 | 2013-04-23 14:22 | Undetermined | Undetermined | 0 | FBK
| 233 | 2013-06-29 18:53 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2013-07-18 08:55 | Undetermined | Undetermined | 0 | FBK
| 233 | 2013-08-31 10:52 | Equipment | Fuse overloaded/inadequate fuse size | 0 | FBK
| 233 | 2013-09-04 11:39 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK
| 233 | 2013-11-07 17:25 | Undetermined | Undetermined | 0 | FBK
| 233 | 2013-12-06 07:47 | Equipment | Conductor failure/wire down | 0 | FBK
| 233 | 2013-12-27 12:56 | Equipment | Arrester (lightning) failure | 0 | FBK
| 233 | 2014-02-28 13:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 233 | 2014-02-28 20:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 233 | 2014-04-01 14:30 | Equipment | Conductor contact/wire slap | 0 | FBK
| 233 | 2014-04-01 15:34 | Equipment | Conductor contact/wire slap | 0 | FBK
| 233 | 2014-04-26 01:32 | Tree Contact | Tree fell on line | 0 | FBK
| 233 | 2014-04-29 09:46 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2014-08-20 06:56 | Customer Contact | Vehicle contact | 0 | FBK
| 233 | 2014-08-20 07:28 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 233 | 2014-10-16 08:16 | Equipment | Fuse overloaded/inadequate fuse size | 0 | FBK
| 233 | 2014-12-16 22:41 | Equipment | Pole broke/rotted/on fire | 0 | FBK
| 235 | 2005-02-25 06:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 235 | 2005-03-02 06:04 | Foreign Object | Bird contact | 0 | RAM
| 235 | 2005-06-12 06:29 | Foreign Object | Bird contact | 0 | RAM
| 235 | 2006-08-25 10:36 | Equipment | Fuse holder/fuse cabinet failed | 0 | RAM
| 235 | 2007-08-26 08:04 | Weather | Lightning Arrester/Transformer failure | 0 | RAM
| 235 | 2007-10-22 08:05 | Weather | Wind - wires slap/pole down | 0 | RAM
| 235 | 2008-01-08 10:11 | Undetermined | Undetermined | 0 | RAM
| 235 | 2008-02-15 08:46 | Foreign Object | Foreign object in distribution line | 0 | RAM
| 235 | 2008-10-01 22:49 | Customer Contact | Vehicle contact | 0 | RAM
| 235 | 2008-11-16 10:26 | Undetermined | Undetermined | 0 | RAM
| 235 | 2010-09-30 12:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 235 | 2010-09-30 15:47 | Weather | Lightning Arrester/Transformer failure | 0 | RAM
| 235 | 2010-10-28 11:27 | Equipment | Cutout failure | 0 | RAM
| 235 | 2010-11-20 11:22 | Equipment | Capacitor failure | 0 | RAM
| 235 | 2011-05-12 15:47 | Foreign Object | Bird contact | 0 | RAM
| 235 | 2011-06-26 16:57 | Undetermined | Undetermined | 0 | RAM
| 235 | 2011-07-01 07:01 | Undetermined | Undetermined | 0 | RAM
| 235 | 2011-08-21 16:10 | Foreign Object | Foreign object in distribution line | 0 | RAM
| 235 | 2011-11-01 19:29 | Undetermined | Undetermined | 0 | RAM
| 235 | 2012-03-27 08:04 | Foreign Object | Bird contact | 0 | RAM
| 235 | 2012-06-08 11:02 | Foreign Object | Bird contact | 0 | RAM
| 235 | 2012-06-28 18:41 | Undetermined | Undetermined | 0 | RAM
| 235 | 2012-08-09 13:51 | Undetermined | Undetermined | 0 | RAM
| 235 | 2013-08-07 10:23 | Foreign Object | Bird contact | 0 | RAM
| 235 | 2013-08-24 09:00 | Equipment | Capacitor failure | 0 | RAM
| 235 | 2014-05-13 02:04 | Customer Contact | Vehicle contact | 0 | RAM
| 235 | 2014-06-19 11:20 | Customer Contact | Vehicle contact | 0 | RAM
| 235 | 2014-07-09 05:04 | Foreign Object | Bird contact | 1 | RAM
| 235 | 2014-07-23 09:34 | Equipment | Arrester (lightning) failure | 0 | RAM
| 236 | 2005-10-20 12:19 | Customer Contact | Vehicle contact | 0 | RAM
| 236 | 2006-06-17 09:39 | Foreign Object | Bird contact | 0 | RAM
| 236 | 2006-12-04 08:09 | Equipment | Transformer faulted/mechanical | 0 | RAM
| 236 | 2006-12-21 00:47 | Equipment | Conductor failure/wire down | 0 | RAM
| 236 | 2007-02-19 19:08 | Undetermined | Undetermined | 0 | RAM
| 236 | 2007-03-04 10:39 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RAM
| 236 | 2007-05-05 09:11 | Undetermined | Undetermined | 0 | RAM
| 236 | 2007-08-26 07:52 | Weather | Lightning Arrester/Transformer failure | 0 | RAM
| 236 | 2007-11-08 13:23 | Undetermined | Undetermined | 0 | RAM
| 236 | 2007-11-28 08:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2007-11-28 14:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2007-11-30 09:10 | Equipment | Pole broke/rotted/on fire | 0 | RAM
| 236 | 2007-12-04 18:22 | Undetermined | Undetermined | 0 | RAM
| 236 | 2007-12-31 19:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2007-12-31 21:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2008-01-01 02:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2008-01-01 03:43 | Equipment | Insulator/pin failure/wire floating | 0 | RAM
| 236 | 2008-01-01 05:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2008-01-01 07:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2008-01-01 08:17 | Weather | Wind - wires slap/pole down | 0 | RAM
| 236 | 2008-03-10 18:50 | Weather | Wind - wires slap/pole down | 0 | RAM
| 236 | 2008-04-11 18:06 | Undetermined | Undetermined | 0 | RAM
| 236 | 2008-07-23 06:31 | Undetermined | Undetermined | 0 | RAM
| 236 | 2008-08-04 15:31 | Customer Contact | Heavy equp contact/digin | 0 | RAM
| 236 | 2008-12-16 06:45 | Equipment | Arrester (lightning) failure | 0 | RAM
| 236 | 2009-05-04 16:58 | Undetermined | Undetermined | 0 | RAM
| 236 | 2009-06-22 07:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RAM
| 236 | 2009-12-07 13:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2009-12-13 00:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2010-01-19 14:06 | Weather | Tree fell on line due to storm/wind | 0 | RAM
| 236 | 2010-01-21 06:44 | Weather | Wind - wires slap/pole down | 0 | RAM
| 236 | 2010-02-01 12:47 | Customer Contact | Vehicle contact | 0 | RAM
| 236 | 2010-04-21 22:41 | Undetermined | Undetermined | 0 | RAM
| 236 | 2010-09-23 10:30 | Customer Contact | Vehicle contact | 0 | RAM
| 236 | 2010-09-30 12:10 | Weather | Lightning Arrester/Transformer failure | 0 | RAM
| 236 | 2010-09-30 13:18 | Weather | Lightning Arrester/Transformer failure | 0 | RAM
| 236 | 2010-10-27 14:58 | Undetermined | Undetermined | 0 | RAM
| 236 | 2011-02-20 15:59 | Weather | Ice or snow/Equipment failure | 0 | RAM
| 236 | 2011-02-21 12:33 | Equipment | Conductor failure/wire down | 0 | RAM
| 236 | 2011-04-05 21:15 | Undetermined | Undetermined | 0 | RAM
| 236 | 2011-05-04 22:52 | Undetermined | Undetermined | 0 | RAM
| 236 | 2011-08-03 21:13 | Undetermined | Undetermined | 0 | RAM
| 236 | 2011-10-27 16:20 | Customer Contact | Vehicle contact | 0 | RAM
| 236 | 2011-11-12 17:07 | Equipment | Hardware failure | 0 | RAM
| 236 | 2012-03-03 14:30 | Foreign Object | Bird contact | 0 | RAM
| 236 | 2012-05-27 01:48 | Undetermined | Undetermined | 0 | RAM
| 236 | 2012-05-28 13:44 | Equipment | Insulator/pin failure/wire floating | 0 | RAM
| 236 | 2012-05-28 17:02 | Undetermined | Undetermined | 0 | RAM
| 236 | 2012-06-15 08:03 | Foreign Object | Bird contact | 0 | RAM
| 236 | 2012-06-26 12:45 | Undetermined | Undetermined | 0 | RAM
| 236 | 2012-11-09 01:19 | Undetermined | Undetermined | 0 | RAM
| 236 | 2012-11-09 23:34 | Equipment | Transformer faulted/mechanical | 0 | RAM
| 236 | 2013-03-10 08:42 | Foreign Object | Bird contact | 0 | RAM
| 236 | 2013-06-19 05:55 | Undetermined | Undetermined | 0 | RAM
| 236 | 2014-02-28 12:29 | Weather | Wind - wires slap/pole down | 0 | RAM
| 236 | 2014-03-02 16:06 | Equipment | Arrester (lightning) failure | 0 | RAM
| 236 | 2014-04-30 10:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2014-05-13 10:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM
| 236 | 2014-05-14 10:04 | Weather | Wind - wires slap/pole down | 0 | RAM
| 236 | 2014-05-16 21:24 | Weather | Tree fell on line due to storm/wind | 0 | RAM
| 236 | 2014-07-25 09:35 | Weather | Lightning Arrester/Transformer failure | 0 | RAM
| 236 | 2014-08-04 00:38 | Undetermined | Undetermined | 0 | RAM
| 237 | 2005-02-24 15:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS
| 237 | 2005-02-24 15:28 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2005-02-24 18:13 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2005-07-12 16:20 | Equipment | Crossarm failure | 1 | GOS
| 237 | 2005-07-16 12:02 | Undetermined | Undetermined | 0 | GOS
| 237 | 2005-07-31 13:15 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2005-07-31 16:20 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2005-08-13 06:52 | Undetermined | Undetermined | 0 | GOS
| 237 | 2006-01-26 11:36 | Customer Contact | Vehicle contact | 0 | GOS
| 237 | 2006-02-27 22:32 | Foreign Object | Foreign object in distribution line | 0 | GOS
| 237 | 2006-03-23 18:06 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2006-04-12 18:17 | Undetermined | Undetermined | 0 | GOS
| 237 | 2006-04-24 11:05 | Undetermined | Undetermined | 0 | GOS
| 237 | 2006-06-24 06:27 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2006-07-30 09:24 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2006-10-23 14:13 | Foreign Object | Foreign object in distribution line | 0 | GOS
| 237 | 2007-05-04 10:30 | Customer Contact | Vehicle contact | 0 | GOS
| 237 | 2007-05-16 18:20 | Equipment | Crossarm failure | 0 | GOS
| 237 | 2007-06-09 11:34 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2007-11-11 08:36 | Equipment | Insulator/pin failure/wire floating | 0 | GOS
| 237 | 2007-11-13 08:43 | Undetermined | Undetermined | 0 | GOS
| 237 | 2007-12-02 12:12 | Undetermined | Undetermined | 0 | GOS
| 237 | 2007-12-31 22:21 | Weather | Wind - wires slap/pole down | 0 | GOS
| 237 | 2008-03-03 07:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS
| 237 | 2008-03-03 08:04 | Weather | Wind - wires slap/pole down | 0 | GOS
| 237 | 2008-04-13 19:02 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS
| 237 | 2008-09-19 22:26 | Tree Contact | Tree fell on line | 0 | GOS
| 237 | 2008-10-03 12:27 | Undetermined | Undetermined | 0 | GOS
| 237 | 2008-10-04 05:10 | Equipment | Conductor contact/wire slap | 0 | GOS
| 237 | 2008-10-31 10:41 | Equipment | Conductor contact/wire slap | 0 | GOS
| 237 | 2008-11-14 14:46 | Weather | Tree contact due to storm/high wind | 0 | GOS
| 237 | 2008-12-09 15:25 | Undetermined | Undetermined | 0 | GOS
| 237 | 2008-12-15 09:58 | Equipment | Conductor contact/wire slap | 0 | GOS
| 237 | 2009-09-19 13:52 | Equipment | Transformer overloaded/electrical | 0 | GOS
| 237 | 2009-10-10 14:38 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2009-12-02 11:31 | Foreign Object | Animal contact | 0 | GOS
| 237 | 2010-01-19 14:05 | Weather | Wind - wires slap/pole down | 0 | GOS
| 237 | 2010-01-21 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS
| 237 | 2010-02-01 13:05 | Customer Contact | Vehicle contact | 0 | GOS
| 237 | 2010-02-05 00:49 | Undetermined | Undetermined | 0 | GOS
| 237 | 2010-07-15 22:50 | Weather | Lightning Arrester/Transformer failure | 1 | GOS
| 237 | 2010-09-13 16:12 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2010-10-07 17:31 | Undetermined | Undetermined | 0 | GOS
| 237 | 2011-02-02 08:12 | Weather | Wind - wires slap/pole down | 0 | GOS
| 237 | 2011-02-21 22:32 | Customer Contact | Vehicle contact | 0 | GOS
| 237 | 2011-03-05 19:06 | Customer Contact | Vehicle contact | 0 | GOS
| 237 | 2011-04-28 00:58 | Undetermined | Undetermined | 0 | GOS
| 237 | 2011-12-12 22:40 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2012-03-29 14:14 | Equipment | Cutout failure | 0 | GOS
| 237 | 2012-09-10 15:11 | Undetermined | Undetermined | 0 | GOS
| 237 | 2012-09-14 14:36 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2012-11-10 12:00 | Undetermined | Undetermined | 0 | GOS
| 237 | 2013-04-08 07:06 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2013-05-23 14:20 | Equipment | Arrester (lightning) failure | 0 | GOS
| 237 | 2013-06-11 04:28 | Undetermined | Undetermined | 0 | GOS
| 237 | 2013-08-29 14:16 | Undetermined | Undetermined | 0 | GOS
| 237 | 2014-05-14 08:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS
| 237 | 2014-08-02 17:58 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2014-08-03 14:21 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2014-08-03 15:48 | Weather | Lightning Arrester/Transformer failure | 0 | GOS
| 237 | 2014-08-17 17:51 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2014-09-25 10:20 | Undetermined | Undetermined | 0 | GOS
| 237 | 2014-11-02 17:19 | Tree Contact | Tree fell on line | 0 | GOS
| 237 | 2014-12-16 10:50 | Foreign Object | Bird contact | 0 | GOS
| 237 | 2015-02-12 20:06 | Tree Contact | Tree fell on line | 0 | GOS
| 237 | 2015-02-23 08:12 | Equipment | Cutout failure | 0 | GOS
| 239 | 2005-02-24 19:37 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2005-04-21 12:53 | Equipment | Conductor failure/wire down | 0 | FBK
| 239 | 2005-09-05 13:48 | Undetermined | Undetermined | 0 | FBK
| 239 | 2005-09-20 06:02 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2005-09-20 19:30 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2005-10-09 23:34 | Customer Contact | Vehicle contact | 0 | FBK
| 239 | 2005-11-13 01:25 | Customer Contact | Vehicle contact | 0 | FBK
| 239 | 2005-11-29 12:10 | Undetermined | Undetermined | 0 | FBK
| 239 | 2005-12-16 18:44 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-01-06 22:24 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-01-23 08:31 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-01-23 09:30 | Weather | Wind - wires slap/pole down | 0 | FBK
| 239 | 2006-02-06 17:43 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-02-26 21:40 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-04-15 13:04 | Equipment | Switch faulted/mechanical | 0 | FBK
| 239 | 2006-06-06 23:07 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-08-18 08:47 | Equipment | Pole broke/rotted/on fire | 0 | FBK
| 239 | 2006-10-10 09:25 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-10-30 08:51 | Customer Contact | Line fault/tree trimming | 0 | FBK
| 239 | 2006-11-18 12:54 | Equipment | Fuse holder/fuse cabinet failed | 0 | FBK
| 239 | 2006-11-19 15:45 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-11-21 07:26 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-11-26 09:50 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-11-28 22:15 | Undetermined | Undetermined | 0 | FBK
| 239 | 2006-11-29 11:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 239 | 2006-12-09 08:43 | Undetermined | Undetermined | 0 | FBK
| 239 | 2007-08-05 11:38 | Tree Contact | Tree fell on line | 0 | FBK
| 239 | 2007-10-13 05:35 | Weather | Tree fell on line due to storm/wind | 0 | FBK
| 239 | 2007-10-29 11:03 | Equipment | Conductor contact/wire slap | 0 | FBK
| 239 | 2008-02-08 10:46 | Customer Contact | Line fault/tree trimming | 0 | FBK
| 239 | 2008-03-10 13:24 | Foreign Object | Damage by gunshot | 0 | FBK
| 239 | 2008-05-22 14:12 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2008-09-19 11:28 | Customer Contact | Vehicle contact | 0 | FBK
| 239 | 2008-09-25 01:19 | Customer Contact | Heavy equp contact/digin | 0 | FBK
| 239 | 2008-09-27 17:02 | Equipment | Switch overloaded/electrical | 0 | FBK
| 239 | 2008-12-14 23:08 | Customer Contact | Vehicle contact | 0 | FBK
| 239 | 2009-01-12 22:49 | Weather | Tree fell on line due to storm/wind | 0 | FBK
| 239 | 2009-01-26 21:35 | Foreign Object | Foreign object in distribution line | 0 | FBK
| 239 | 2009-01-26 23:50 | Foreign Object | Foreign object in distribution line | 0 | FBK
| 239 | 2009-03-09 18:39 | Foreign Object | Foreign object in distribution line | 0 | FBK
| 239 | 2009-04-04 05:25 | Foreign Object | Foreign object in distribution line | 0 | FBK
| 239 | 2009-06-03 09:50 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2009-06-03 13:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 239 | 2009-06-03 16:16 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2009-11-28 14:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK
| 239 | 2009-12-07 17:08 | Weather | Wind - wires slap/pole down | 0 | FBK
| 239 | 2010-01-21 22:58 | Weather | Wind - wires slap/pole down | 0 | FBK
| 239 | 2010-02-27 19:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK
| 239 | 2010-04-02 20:09 | Undetermined | Undetermined | 0 | FBK
| 239 | 2010-05-01 09:54 | Foreign Object | Bird contact | 0 | FBK
| 239 | 2010-05-03 09:32 | Foreign Object | Foreign object in distribution line | 0 | FBK
| 239 | 2010-06-01 08:48 | Undetermined | Undetermined | 0 | FBK
| 239 | 2010-07-15 15:39 | Weather | Lightning Arrester/Transformer failure | 1 | FBK
| 239 | 2010-10-04 20:01 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2010-10-13 13:57 | Undetermined | Undetermined | 0 | FBK
| 239 | 2010-12-22 15:07 | Weather | Tree fell on line due to storm/wind | 0 | FBK
| 239 | 2011-02-19 22:43 | Equipment | Conductor failure/wire down | 0 | FBK
| 239 | 2011-03-01 08:45 | Equipment | Conductor failure/wire down | 0 | FBK
| 239 | 2011-05-19 16:55 | Tree Contact | Tree fell on line | 0 | FBK
| 239 | 2012-03-20 06:38 | Undetermined | Undetermined | 0 | FBK
| 239 | 2012-04-26 11:51 | Weather | Lightning Arrester/Transformer failure | 0 | FBK
| 239 | 2012-07-05 08:17 | Foreign Object | Bird contact | 1 | FBK
| 239 | 2012-08-15 19:26 | Undetermined | Undetermined | 0 | FBK
| 239 | 2012-09-04 19:03 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK
| 239 | 2012-12-31 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK
| 239 | 2013-04-08 19:25 | Foreign Object | Bird contact | 0 | FBK
| 239 | 2013-05-01 15:00 | Equipment | Transformer faulted/mechanical | 0 | FBK
| 239 | 2013-09-20 18:43 | Undetermined | Undetermined | 0 | FBK
| 239 | 2013-12-07 14:59 | Equipment | Conductor failure/wire down | 0 | FBK
| 239 | 2014-01-24 07:24 | Customer Contact | Vehicle contact | 0 | FBK
| 239 | 2014-04-29 06:51 | Equipment | Regulator faulted/mechanical | 0 | FBK
| 239 | 2014-07-25 21:31 | Equipment | Conductor failure/wire down | 0 | FBK
| 239 | 2014-09-16 15:52 | Equipment | Conductor failure/wire down | 0 | FBK
| 239 | 2014-12-24 10:45 | Foreign Object | Bird contact | 0 | FBK
| 239 | 2014-12-27 06:05 | Foreign Object | Damage by gunshot | 0 | FBK
| 239 | 2015-01-08 13:56 | Undetermined | Undetermined | 0 | FBK
| 239 | 2015-01-08 22:40 | Equipment | Fuse holder/fuse cabinet failed | 0 | FBK
| 240 | 2005-01-19 20:08 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2005-07-23 03:32 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 240 | 2005-07-23 04:16 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 240 | 2005-07-23 06:07 | Weather | Wind - wires slap/pole down | 0 | BVY
| 240 | 2005-07-23 06:22 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 240 | 2005-07-23 06:22 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 240 | 2005-07-27 06:03 | Undetermined | Undetermined | 0 | BVY
| 240 | 2005-09-22 11:36 | Foreign Object | Bird contact | 0 | BVY
| 240 | 2005-11-10 13:11 | Undetermined | Undetermined | 0 | BVY
| 240 | 2006-01-01 04:36 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2006-01-04 14:36 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 240 | 2006-03-05 09:02 | Undetermined | Undetermined | 0 | BVY
| 240 | 2006-08-23 08:50 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2006-09-08 13:11 | Undetermined | Undetermined | 0 | BVY
| 240 | 2006-09-20 11:34 | Equipment | Conductor failure/wire down | 0 | BVY
| 240 | 2006-11-27 12:03 | Undetermined | Undetermined | 0 | BVY
| 240 | 2007-03-01 08:11 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 240 | 2007-04-02 00:12 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2007-10-20 18:15 | Foreign Object | Bird contact | 0 | BVY
| 240 | 2007-11-05 08:59 | Equipment | Capacitor failure | 0 | BVY
| 240 | 2008-09-07 04:31 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2008-12-01 07:36 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2008-12-09 12:10 | Foreign Object | Foreign object in distribution line | 0 | BVY
| 240 | 2008-12-15 14:19 | Undetermined | Undetermined | 0 | BVY
| 240 | 2009-02-09 17:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2009-10-08 11:05 | Tree Contact | Tree fell on line | 0 | BVY
| 240 | 2009-12-07 15:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2010-01-19 15:12 | Weather | Wind - wires slap/pole down | 0 | BVY
| 240 | 2010-07-02 13:43 | Foreign Object | Bird contact | 1 | BVY
| 240 | 2010-09-29 09:14 | Equipment | Transformer faulted/mechanical | 0 | BVY
| 240 | 2010-09-30 12:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2010-09-30 13:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2010-09-30 17:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2010-09-30 22:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2010-10-25 13:35 | Equipment | Crossarm failure | 0 | BVY
| 240 | 2010-11-22 03:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVY
| 240 | 2010-12-24 18:17 | Equipment | Switch faulted/mechanical | 0 | BVY
| 240 | 2011-01-23 07:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2011-02-02 13:11 | Weather | Wind - wires slap/pole down | 0 | BVY
| 240 | 2011-03-28 09:03 | Undetermined | Undetermined | 0 | BVY
| 240 | 2011-05-11 16:59 | Foreign Object | Bird contact | 0 | BVY
| 240 | 2011-05-26 07:57 | Foreign Object | Bird contact | 0 | BVY
| 240 | 2011-08-01 03:18 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2011-08-03 08:48 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 240 | 2011-09-14 23:13 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2011-10-05 23:38 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2011-10-26 16:44 | Foreign Object | Bird contact | 0 | BVY
| 240 | 2011-11-28 06:32 | Foreign Object | Bird contact | 0 | BVY
| 240 | 2012-01-26 14:11 | Foreign Object | Foreign object in distribution line | 0 | BVY
| 240 | 2012-02-12 10:50 | Tree Contact | Tree fell on line | 0 | BVY
| 240 | 2012-03-01 09:25 | Equipment | Conductor failure/wire down | 0 | BVY
| 240 | 2012-03-02 08:59 | Undetermined | Undetermined | 0 | BVY
| 240 | 2012-03-18 11:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2012-03-18 12:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2012-03-30 18:09 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2012-09-14 08:38 | Weather | Wind - wires slap/pole down | 0 | BVY
| 240 | 2012-09-14 11:13 | Equipment | Conductor contact/wire slap | 0 | BVY
| 240 | 2013-01-22 11:21 | Equipment | Flashover/equip contam/overload | 0 | BVY
| 240 | 2013-01-26 05:52 | Equipment | Arrester (lightning) failure | 0 | BVY
| 240 | 2013-02-08 06:51 | Foreign Object | Flashover/vegetation | 0 | BVY
| 240 | 2013-02-10 01:54 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2013-06-18 08:21 | Equipment | Conductor failure/wire down | 0 | BVY
| 240 | 2013-10-04 01:18 | Undetermined | Undetermined | 0 | BVY
| 240 | 2013-10-04 07:06 | Undetermined | Undetermined | 0 | BVY
| 240 | 2013-12-05 08:28 | Customer Contact | Vehicle contact | 0 | BVY
| 240 | 2013-12-18 10:40 | Undetermined | Undetermined | 0 | BVY
| 240 | 2014-01-03 07:45 | Foreign Object | Animal contact | 0 | BVY
| 240 | 2014-02-06 19:30 | Equipment | Cutout failure | 0 | BVY
| 240 | 2014-02-28 18:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2014-04-30 13:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 240 | 2015-01-25 10:08 | Undetermined | Undetermined | 0 | BVY
| 243 | 2005-07-13 13:50 | Equipment | Cutout failure | 1 | BVY
| 243 | 2005-12-31 16:28 | Equipment | Transformer faulted/mechanical | 0 | BVY
| 243 | 2006-01-24 22:28 | Equipment | Cutout failure | 0 | BVY
| 243 | 2006-02-07 10:19 | Equipment | Fuse holder/fuse cabinet failed | 0 | BVY
| 243 | 2006-04-19 15:47 | Customer Contact | Line fault/tree trimming | 0 | BVY
| 243 | 2006-07-24 19:25 | Equipment | Fuse overloaded/inadequate fuse size | 0 | BVY
| 243 | 2007-04-22 15:33 | Undetermined | Undetermined | 0 | BVY
| 243 | 2007-05-18 06:47 | Foreign Object | Bird contact | 0 | BVY
| 243 | 2007-05-27 19:00 | Undetermined | Undetermined | 0 | BVY
| 243 | 2008-01-23 19:14 | Weather | Tree fell on line due to storm/wind | 0 | BVY
| 243 | 2008-03-13 13:17 | Equipment | Arrester (lightning) failure | 0 | BVY
| 243 | 2008-09-09 09:26 | Customer Contact | Line fault/tree trimming | 0 | BVY
| 243 | 2009-05-08 04:21 | Undetermined | Undetermined | 0 | BVY
| 243 | 2010-01-21 12:17 | Weather | Tree fell on line due to storm/wind | 0 | BVY
| 243 | 2010-09-30 13:12 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 243 | 2010-09-30 13:41 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 243 | 2010-10-01 13:03 | Equipment | Capacitor failure | 0 | BVY
| 243 | 2011-02-02 13:38 | Weather | Tree fell on line due to storm/wind | 0 | BVY
| 243 | 2011-10-04 17:12 | Foreign Object | Foreign object in distribution line | 0 | BVY
| 243 | 2011-11-08 12:22 | Equipment | Transformer faulted/mechanical | 0 | BVY
| 243 | 2011-12-23 00:47 | Customer Contact | Vehicle contact | 0 | BVY
| 243 | 2012-05-20 19:34 | Customer Contact | Line fault/tree trimming | 0 | BVY
| 243 | 2013-10-29 10:32 | Equipment | Pole broke/rotted/on fire | 0 | BVY
| 243 | 2014-01-14 23:54 | Customer Contact | Vehicle contact | 0 | BVY
| 243 | 2014-04-12 04:20 | Customer Contact | Vehicle contact | 0 | BVY
| 243 | 2014-05-24 08:26 | Equipment | Fuse holder/fuse cabinet failed | 0 | BVY
| 243 | 2014-11-19 09:27 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 243 | 2014-11-19 09:56 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 243 | 2014-11-25 10:36 | Customer Contact | Vehicle contact | 0 | BVY
| 246 | 2005-01-29 15:25 | Undetermined | Undetermined | 0 | BVY
| 246 | 2005-06-09 14:35 | Customer Contact | Vehicle contact | 0 | BVY
| 246 | 2005-09-20 12:09 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 246 | 2006-07-23 16:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 246 | 2006-08-26 16:42 | Equipment | Transformer faulted/mechanical | 0 | BVY
| 246 | 2007-06-14 20:33 | Customer Contact | Vehicle contact | 0 | BVY
| 246 | 2007-11-08 03:57 | Undetermined | Undetermined | 0 | BVY
| 246 | 2008-02-29 12:32 | Undetermined | Undetermined | 0 | BVY
| 246 | 2008-03-30 00:42 | Equipment | Insulator/pin failure/wire floating | 0 | BVY
| 246 | 2008-09-13 13:22 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 246 | 2009-11-25 08:48 | Foreign Object | Bird contact | 0 | BVY
| 246 | 2010-08-19 10:36 | Undetermined | Undetermined | 0 | BVY
| 246 | 2010-09-16 17:54 | Undetermined | Undetermined | 0 | BVY
| 246 | 2010-09-26 14:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 246 | 2010-09-30 13:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY
| 246 | 2010-09-30 17:33 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 246 | 2010-10-01 20:13 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 246 | 2010-12-26 03:15 | Weather | Tree fell on line due to storm/wind | 0 | BVY
| 246 | 2011-10-07 18:35 | Equipment | Fuse holder/fuse cabinet failed | 0 | BVY
| 246 | 2011-12-16 09:20 | Equipment | Pole broke/rotted/on fire | 0 | BVY
| 246 | 2012-01-23 15:04 | Undetermined | Undetermined | 0 | BVY
| 246 | 2012-02-27 20:50 | Weather | Lightning Arrester/Transformer failure | 0 | BVY
| 246 | 2012-09-23 18:44 | Equipment | Transformer faulted/mechanical | 0 | BVY
| 246 | 2013-03-20 20:10 | Undetermined | Undetermined | 0 | BVY
| 246 | 2013-04-05 00:32 | Equipment | Conductor failure/wire down | 0 | BVY
| 246 | 2014-01-08 06:58 | Foreign Object | Bird contact | 0 | BVY
| 246 | 2014-01-15 06:53 | Undetermined | Undetermined | 0 | BVY
| 246 | 2014-03-12 06:52 | Customer Contact | Vehicle contact | 0 | BVY
| 246 | 2014-06-04 15:55 | Equipment | Crossarm failure | 0 | BVY
| 246 | 2014-11-11 07:51 | Customer Contact | Line fault/tree trimming | 0 | BVY
| 246 | 2014-11-19 09:27 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 246 | 2014-11-19 09:56 | Customer Contact | Heavy equp contact/digin | 0 | BVY
| 246 | 2015-03-01 20:40 | Undetermined | Undetermined | 0 | BVY
| 283 | 2005-01-30 15:02 | Equipment | Transformer faulted/mechanical | 0 | LLD
| 283 | 2005-02-08 13:22 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2005-02-11 10:39 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2005-05-04 12:52 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2005-05-13 06:21 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2005-09-19 08:10 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2007-06-11 08:31 | Undetermined | Undetermined | 0 | LLD
| 283 | 2007-06-17 06:55 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD
| 283 | 2007-08-17 22:37 | Undetermined | Undetermined | 0 | LLD
| 283 | 2007-11-23 19:10 | Undetermined | Undetermined | 0 | LLD
| 283 | 2008-02-08 02:33 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2008-05-13 07:50 | Undetermined | Undetermined | 0 | LLD
| 283 | 2008-08-14 15:57 | Undetermined | Undetermined | 0 | LLD
| 283 | 2008-09-14 10:12 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2009-06-20 06:01 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2009-08-30 09:00 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2009-10-05 23:40 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2009-10-12 00:15 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2009-12-08 08:36 | Weather | Wind - wires slap/pole down | 0 | LLD
| 283 | 2010-06-14 21:28 | Weather | Earthquake | 0 | LLD
| 283 | 2010-10-18 09:13 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2012-05-28 18:21 | Undetermined | Undetermined | 0 | LLD
| 283 | 2012-12-07 20:36 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD
| 283 | 2012-12-15 07:16 | Weather | Lightning Arrester/Transformer failure | 0 | LLD
| 283 | 2013-03-10 00:55 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2013-04-14 22:10 | Equipment | Transformer faulted/mechanical | 0 | LLD
| 283 | 2013-05-12 13:08 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD
| 283 | 2013-06-05 17:56 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2013-06-22 07:54 | Equipment | Cutout failure | 0 | LLD
| 283 | 2013-06-22 08:50 | Equipment | Cutout failure | 0 | LLD
| 283 | 2013-07-21 16:27 | Undetermined | Undetermined | 0 | LLD
| 283 | 2013-11-05 14:07 | Foreign Object | Bird contact | 0 | LLD
| 283 | 2014-02-04 18:43 | Customer Contact | Line fault/tree trimming | 0 | LLD
| 283 | 2014-07-22 10:12 | Customer Contact | Vehicle contact | 0 | LLD
| 283 | 2014-07-27 09:08 | Weather | Lightning Arrester/Transformer failure | 0 | LLD
| 283 | 2014-12-04 05:21 | Undetermined | Undetermined | 0 | LLD
| 283 | 2014-12-12 11:27 | Undetermined | Undetermined | 0 | LLD
| 283 | 2015-02-17 09:05 | Equipment | Cutout failure | 0 | LLD
| 305 | 2005-09-20 00:44 | Weather | Lightning Arrester/Transformer failure | 0 | RSF
| 305 | 2006-06-10 21:25 | Tree Contact | Tree fell on line | 0 | RSF
| 305 | 2006-08-29 11:25 | Equipment | Cutout failure | 0 | RSF
| 305 | 2006-11-29 22:51 | Weather | Tree fell on line due to storm/wind | 0 | RSF
| 305 | 2008-01-31 12:21 | Equipment | Fuse holder/fuse cabinet failed | 0 | RSF
| 305 | 2008-02-26 22:14 | Customer Contact | Vehicle contact | 0 | RSF
| 305 | 2008-04-16 11:49 | Foreign Object | Bird contact | 0 | RSF
| 305 | 2008-05-23 18:02 | Customer Contact | Vehicle contact | 0 | RSF
| 305 | 2008-12-19 00:37 | Undetermined | Undetermined | 0 | RSF
| 305 | 2009-02-03 00:50 | Customer Contact | Vehicle contact | 0 | RSF
| 305 | 2009-02-09 16:47 | Weather | Tree fell on line due to storm/wind | 0 | RSF
| 305 | 2009-02-25 06:07 | Undetermined | Undetermined | 0 | RSF
| 305 | 2009-04-10 21:44 | Weather | Lightning Arrester/Transformer failure | 0 | RSF
| 305 | 2009-04-10 23:59 | Weather | Lightning Arrester/Transformer failure | 0 | RSF
| 305 | 2009-07-13 22:07 | Equipment | Conductor failure/wire down | 1 | RSF
| 305 | 2009-12-07 17:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF
| 305 | 2012-01-11 18:06 | Customer Contact | Vehicle contact | 0 | RSF
| 305 | 2012-08-14 14:46 | Undetermined | Undetermined | 0 | RSF
| 305 | 2013-02-01 16:15 | Undetermined | Undetermined | 0 | RSF
| 305 | 2013-05-02 10:24 | Equipment | Cutout failure | 0 | RSF
| 305 | 2014-09-05 20:18 | Customer Contact | Vehicle contact | 0 | RSF
| 307 | 2005-02-19 16:49 | Weather | Tree fell on line due to storm/wind | 0 | RSF
| 307 | 2008-02-22 11:53 | Tree Contact | Tree fell on line | 0 | RSF
| 307 | 2009-02-23 19:29 | Undetermined | Undetermined | 0 | RSF
| 307 | 2009-06-04 18:22 | Equipment | Transformer faulted/mechanical | 0 | RSF
| 307 | 2012-03-18 05:06 | Weather | Tree fell on line due to storm/wind | 0 | RSF
| 311 | 2006-02-07 21:34 | Weather | Tree fell on line due to storm/wind | 0 | CAP
| 311 | 2006-02-28 08:27 | Equipment | Transformer faulted/mechanical | 0 | CAP
| 311 | 2008-05-27 14:00 | Equipment | Arrester (lightning) failure | 0 | CAP
| 311 | 2010-01-21 15:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP
| 311 | 2010-09-25 23:18 | Undetermined | Undetermined | 0 | CAP
| 311 | 2011-10-02 15:17 | Undetermined | Undetermined | 0 | CAP
| 311 | 2011-11-17 12:23 | Undetermined | Undetermined | 0 | CAP
| 311 | 2011-12-29 07:48 | Customer Contact | Vehicle contact | 0 | CAP
| 311 | 2014-01-15 08:47 | Foreign Object | Animal contact | 0 | CAP
| 311 | 2014-12-12 04:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP
| 311 | 2014-12-30 21:30 | Equipment | Conductor failure/wire down | 0 | CAP
| 320 | 2010-09-18 14:32 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 320 | 2011-11-20 21:40 | Equipment | Transformer faulted/mechanical | 0 | MIG
| 320 | 2014-04-04 00:28 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 320 | 2014-05-13 01:07 | Customer Contact | Vehicle contact | 0 | MIG
| 320 | 2014-09-24 20:36 | Undetermined | Undetermined | 0 | MIG
| 321 | 2005-10-06 13:14 | Foreign Object | Bird contact | 0 | MIG
| 321 | 2005-11-15 10:19 | Customer Contact | Vehicle contact | 0 | MIG
| 321 | 2005-12-29 08:06 | Foreign Object | Bird contact | 0 | MIG
| 321 | 2007-01-04 20:05 | Equipment | Capacitor failure | 0 | MIG
| 321 | 2007-01-04 21:12 | Equipment | Capacitor failure | 0 | MIG
| 321 | 2007-02-05 11:21 | Equipment | Cutout failure | 0 | MIG
| 321 | 2008-09-16 12:55 | Equipment | Capacitor failure | 0 | MIG
| 321 | 2008-12-09 10:29 | Weather | Lightning Arrester/Transformer failure | 0 | MIG
| 321 | 2009-12-06 19:18 | Equipment | Capacitor failure | 0 | MIG
| 321 | 2009-12-07 17:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MIG
| 321 | 2010-01-19 13:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MIG
| 321 | 2010-05-19 09:59 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 321 | 2010-08-24 23:56 | Undetermined | Undetermined | 0 | MIG
| 321 | 2011-07-13 15:09 | Foreign Object | Foreign object in distribution line | 1 | MIG
| 321 | 2011-07-29 14:24 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 321 | 2013-09-04 00:31 | Equipment | Transformer faulted/mechanical | 0 | MIG
| 321 | 2014-03-10 16:19 | Equipment | Cutout failure | 0 | MIG
| 321 | 2014-05-13 22:28 | Customer Contact | Vehicle contact | 0 | MIG
| 321 | 2014-05-29 08:33 | Foreign Object | Bird contact | 0 | MIG
| 322 | 2005-10-31 06:08 | Undetermined | Undetermined | 0 | MIG
| 322 | 2006-03-24 21:01 | Equipment | Transformer faulted/mechanical | 0 | MIG
| 322 | 2006-04-04 16:21 | Foreign Object | Bird contact | 0 | MIG
| 322 | 2008-03-27 06:59 | Customer Contact | Vehicle contact | 0 | MIG
| 322 | 2008-04-11 14:12 | Equipment | Transformer faulted/mechanical | 0 | MIG
| 322 | 2008-11-18 15:54 | Undetermined | Undetermined | 0 | MIG
| 322 | 2008-11-29 18:53 | Undetermined | Undetermined | 0 | MIG
| 322 | 2008-12-16 10:26 | Equipment | Crossarm failure | 0 | MIG
| 322 | 2008-12-28 05:17 | Undetermined | Undetermined | 0 | MIG
| 322 | 2009-06-27 11:33 | Foreign Object | Bird contact | 0 | MIG
| 322 | 2009-07-03 15:27 | Foreign Object | Foreign object in distribution line | 1 | MIG
| 322 | 2010-06-17 15:07 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 322 | 2010-07-02 01:30 | Equipment | Arrester (lightning) failure | 1 | MIG
| 322 | 2011-03-03 13:02 | Undetermined | Undetermined | 0 | MIG
| 322 | 2011-03-05 23:01 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 322 | 2012-04-28 22:54 | Foreign Object | Bird contact | 0 | MIG
| 322 | 2013-04-01 22:33 | Undetermined | Undetermined | 0 | MIG
| 322 | 2014-02-28 11:28 | Equipment | Switch faulted/mechanical | 0 | MIG
| 322 | 2014-03-26 20:26 | Equipment | Fuse overloaded/inadequate fuse size | 0 | MIG
| 322 | 2014-08-22 12:18 | Equipment | Cutout failure | 0 | MIG
| 322 | 2014-09-16 13:26 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 322 | 2014-10-05 17:15 | Undetermined | Undetermined | 0 | MIG
| 323 | 2005-03-01 14:33 | Equipment | Fuse overloaded/inadequate fuse size | 0 | MIG
| 323 | 2007-01-04 21:03 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MIG
| 323 | 2007-12-31 23:54 | Foreign Object | Damage by gunshot | 0 | MIG
| 323 | 2009-07-29 15:56 | Foreign Object | Foreign object in distribution line | 0 | MIG
| 323 | 2010-02-04 12:26 | Equipment | Fuse overloaded/inadequate fuse size | 0 | MIG
| 323 | 2012-08-08 10:26 | Customer Contact | Line fault/tree trimming | 0 | MIG
| 323 | 2014-04-10 05:54 | Undetermined | Undetermined | 0 | MIG
| 323 | 2014-04-29 16:48 | Weather | Tree fell on line due to storm/wind | 0 | MIG
| 323 | 2014-09-05 04:29 | Undetermined | Undetermined | 0 | MIG
| 323 | 2014-09-30 16:09 | Equipment | Arrester (lightning) failure | 0 | MIG
| 323 | 2015-02-03 23:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MIG
| 324 | 2013-04-22 11:34 | Undetermined | Undetermined | 0 | MIG
| 324 | 2014-04-15 05:54 | Equipment | Guy wire failure | 0 | MIG
| 324 | 2014-04-15 10:27 | Equipment | Guy wire failure | 0 | MIG
| 339 | 2005-03-24 09:15 | Equipment | Pole broke/rotted/on fire | 0 | CAP
| 339 | 2006-11-11 10:24 | Undetermined | Undetermined | 0 | CAP
| 339 | 2008-06-13 18:04 | Foreign Object | Bird contact | 0 | CAP
| 339 | 2010-10-19 07:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP
| 339 | 2011-07-31 06:49 | Weather | Lightning Arrester/Transformer failure | 0 | CAP
| 339 | 2012-03-18 20:51 | Foreign Object | Bird contact | 0 | CAP
| 339 | 2012-12-18 14:53 | Foreign Object | Foreign object in distribution line | 0 | CAP
| 350 | 2005-01-20 10:38 | Undetermined | Undetermined | 0 | LLC
| 350 | 2005-04-22 07:35 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2005-05-02 16:13 | Weather | Palm frond contact due to storm/wind | 0 | LLC
| 350 | 2005-07-23 02:27 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 02:51 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 03:07 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 03:14 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 03:21 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 03:27 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 07:42 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 07:51 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-07-23 07:58 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-08-13 15:14 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2005-09-20 01:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2005-09-20 05:33 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-09-20 18:20 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2005-12-05 12:20 | Undetermined | Undetermined | 0 | LLC
| 350 | 2006-01-02 10:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2006-01-02 12:55 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 350 | 2006-01-02 20:11 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2006-01-02 23:26 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2006-01-10 19:41 | Undetermined | Undetermined | 0 | LLC
| 350 | 2006-02-28 06:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2006-03-10 13:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2006-03-11 07:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2006-06-26 14:29 | Equipment | Insulator/pin failure/wire floating | 0 | LLC
| 350 | 2006-06-28 18:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 350 | 2006-08-30 05:50 | Undetermined | Undetermined | 0 | LLC
| 350 | 2006-10-14 01:11 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2006-10-17 17:38 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2006-10-26 15:27 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2006-12-12 12:57 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 350 | 2006-12-19 15:56 | Undetermined | Undetermined | 0 | LLC
| 350 | 2007-01-26 16:30 | Foreign Object | Damage by gunshot | 0 | LLC
| 350 | 2007-05-18 13:36 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 350 | 2007-06-16 22:36 | Undetermined | Undetermined | 0 | LLC
| 350 | 2007-07-22 16:08 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2007-10-13 05:27 | Undetermined | Undetermined | 0 | LLC
| 350 | 2008-01-27 05:35 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2008-02-19 10:00 | Undetermined | Undetermined | 0 | LLC
| 350 | 2008-06-07 10:50 | Undetermined | Undetermined | 0 | LLC
| 350 | 2008-07-10 13:36 | Customer Contact | Vehicle contact | 1 | LLC
| 350 | 2008-07-17 05:06 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2008-07-19 10:49 | Undetermined | Undetermined | 0 | LLC
| 350 | 2008-09-02 12:53 | Undetermined | Undetermined | 0 | LLC
| 350 | 2008-11-06 10:46 | Undetermined | Undetermined | 0 | LLC
| 350 | 2008-12-15 12:57 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 350 | 2008-12-17 12:55 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 350 | 2008-12-18 02:51 | Undetermined | Undetermined | 0 | LLC
| 350 | 2009-02-09 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2009-02-16 22:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 350 | 2009-05-05 08:23 | Customer Contact | Line fault/tree trimming | 0 | LLC
| 350 | 2009-05-31 21:02 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2009-06-03 10:08 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2009-06-03 11:42 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2009-06-11 14:40 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2009-06-15 13:04 | Equipment | Switch faulted/mechanical | 0 | LLC
| 350 | 2009-07-22 23:08 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 350 | 2009-08-05 13:40 | Equipment | Crossarm failure | 0 | LLC
| 350 | 2009-08-30 17:11 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2009-10-14 07:00 | Undetermined | Undetermined | 0 | LLC
| 350 | 2009-11-29 09:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2009-12-07 14:21 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2009-12-07 17:35 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2009-12-07 21:40 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2009-12-09 11:18 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2009-12-13 09:23 | Undetermined | Undetermined | 0 | LLC
| 350 | 2010-01-12 14:14 | Undetermined | Undetermined | 0 | LLC
| 350 | 2010-01-18 13:31 | Weather | Tree contact due to storm/high wind | 0 | LLC
| 350 | 2010-01-19 14:00 | Weather | Tree contact due to storm/high wind | 0 | LLC
| 350 | 2010-01-19 14:45 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2010-01-21 12:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2010-01-21 15:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2010-01-22 08:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2010-01-22 18:06 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-01-31 10:21 | Equipment | Crossarm failure | 0 | LLC
| 350 | 2010-02-16 15:05 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 350 | 2010-02-17 21:36 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2010-05-08 22:15 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2010-05-13 06:03 | Undetermined | Undetermined | 0 | LLC
| 350 | 2010-05-25 09:21 | Equipment | Hardware failure | 0 | LLC
| 350 | 2010-06-18 11:52 | Undetermined | Undetermined | 0 | LLC
| 350 | 2010-08-04 15:26 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2010-09-02 12:34 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2010-10-04 18:15 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-10-19 02:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2010-10-19 05:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2010-10-19 07:28 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-10-19 08:51 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-10-19 08:51 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-10-19 09:36 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-10-19 16:03 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2010-12-20 05:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2010-12-20 17:35 | Weather | Ice or snow/Equipment failure | 0 | LLC
| 350 | 2011-02-16 14:05 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2011-03-09 14:25 | Equipment | Conductor failure/wire down | 0 | LLC
| 350 | 2011-05-20 12:33 | Undetermined | Undetermined | 0 | LLC
| 350 | 2011-05-30 17:26 | Tree Contact | Tree contact | 0 | LLC
| 350 | 2011-06-29 19:41 | Undetermined | Undetermined | 0 | LLC
| 350 | 2011-09-05 10:42 | Weather | Wind - wires slap/pole down | 0 | LLC
| 350 | 2011-10-05 19:13 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2011-10-05 20:28 | Equipment | Regulator faulted/mechanical | 0 | LLC
| 350 | 2011-10-12 13:53 | Undetermined | Undetermined | 0 | LLC
| 350 | 2011-12-27 22:39 | Customer Contact | Vehicle contact | 0 | LLC
| 350 | 2012-02-14 06:04 | Foreign Object | Flashover/vegetation | 0 | LLC
| 350 | 2012-03-12 13:19 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 350 | 2012-06-30 12:41 | Undetermined | Undetermined | 0 | LLC
| 350 | 2012-07-28 09:50 | Undetermined | Undetermined | 0 | LLC
| 350 | 2012-09-09 16:10 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2012-09-09 22:47 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2012-09-10 04:15 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2012-09-11 10:18 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2012-10-21 13:19 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2012-12-13 13:58 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2012-12-30 11:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2013-03-19 16:48 | Undetermined | Undetermined | 0 | LLC
| 350 | 2013-03-27 08:55 | Undetermined | Undetermined | 0 | LLC
| 350 | 2013-06-07 06:34 | Equipment | Insulator/pin failure/wire floating | 0 | LLC
| 350 | 2013-06-14 18:43 | Equipment | Arrester (lightning) failure | 0 | LLC
| 350 | 2013-09-13 02:06 | Foreign Object | Damage by gunshot | 0 | LLC
| 350 | 2013-09-27 18:01 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2013-12-21 07:32 | Foreign Object | Bird contact | 0 | LLC
| 350 | 2014-03-01 02:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 350 | 2014-03-01 10:15 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2014-04-23 12:17 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 350 | 2014-05-27 18:25 | Equipment | Fuse overloaded/inadequate fuse size | 0 | LLC
| 350 | 2014-05-27 23:57 | Equipment | Fuse overloaded/inadequate fuse size | 0 | LLC
| 350 | 2014-08-20 06:39 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 350 | 2014-09-11 11:56 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2014-09-17 15:22 | Undetermined | Undetermined | 0 | LLC
| 350 | 2014-10-16 21:42 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2014-11-01 08:10 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 350 | 2014-12-03 00:31 | Undetermined | Undetermined | 0 | LLC
| 350 | 2014-12-17 04:08 | Undetermined | Undetermined | 0 | LLC
| 351 | 2005-04-06 18:30 | Tree Contact | Tree fell on line | 0 | TLK
| 351 | 2005-09-20 02:38 | Weather | Lightning Arrester/Transformer failure | 0 | TLK
| 351 | 2005-11-27 04:35 | Equipment | Conductor failure/wire down | 0 | TLK
| 351 | 2006-02-14 12:08 | Customer Contact | Vehicle contact | 0 | TLK
| 351 | 2006-03-18 12:23 | Weather | Wind - wires slap/pole down | 0 | TLK
| 351 | 2006-11-29 17:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK
| 351 | 2006-11-29 20:54 | Weather | Tree fell on line due to storm/wind | 0 | TLK
| 351 | 2007-01-05 17:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK
| 351 | 2007-02-17 12:45 | Tree Contact | Tree fell on line | 0 | TLK
| 351 | 2007-03-04 09:24 | Weather | Tree fell on line due to storm/wind | 0 | TLK
| 351 | 2007-10-22 03:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK
| 351 | 2008-04-17 14:14 | Customer Contact | Line fault/tree trimming | 0 | TLK
| 351 | 2008-06-26 17:29 | Undetermined | Undetermined | 0 | TLK
| 351 | 2008-12-15 01:36 | Equipment | Connector/jumper/splice/elbow/rack | 0 | TLK
| 351 | 2009-11-30 01:04 | Undetermined | Undetermined | 0 | TLK
| 351 | 2010-01-21 14:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK
| 351 | 2010-07-15 19:55 | Weather | Lightning Arrester/Transformer failure | 1 | TLK
| 351 | 2011-11-12 17:39 | Foreign Object | Bird contact | 0 | TLK
| 351 | 2012-04-13 14:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK
| 351 | 2012-04-13 16:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK
| 351 | 2012-06-18 07:13 | Foreign Object | Bird contact | 0 | TLK
| 351 | 2012-09-09 16:22 | Weather | Lightning Arrester/Transformer failure | 0 | TLK
| 351 | 2012-12-29 22:05 | Weather | Tree fell on line due to storm/wind | 0 | TLK
| 351 | 2013-03-08 13:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | TLK
| 351 | 2013-03-11 12:24 | Foreign Object | Bird contact | 0 | TLK
| 351 | 2013-03-20 10:27 | Equipment | Connector/jumper/splice/elbow/rack | 0 | TLK
| 351 | 2014-02-08 14:47 | Customer Contact | Heavy equp contact/digin | 0 | TLK
| 351 | 2014-07-08 16:41 | Customer Contact | Vehicle contact | 1 | TLK
| 351 | 2014-12-26 08:50 | Undetermined | Undetermined | 0 | TLK
| 351 | 2015-03-10 18:23 | Tree Contact | Tree fell on line | 0 | TLK
| 352 | 2005-02-24 18:03 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 352 | 2005-06-21 07:50 | Tree Contact | Tree fell on line | 0 | LLC
| 352 | 2005-08-06 02:45 | Undetermined | Undetermined | 0 | LLC
| 352 | 2006-01-02 12:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 352 | 2006-07-30 02:48 | Undetermined | Undetermined | 0 | LLC
| 352 | 2006-08-07 06:14 | Undetermined | Undetermined | 0 | LLC
| 352 | 2006-08-25 10:00 | Foreign Object | Bird contact | 0 | LLC
| 352 | 2006-11-25 10:57 | Undetermined | Undetermined | 0 | LLC
| 352 | 2006-12-27 11:49 | Weather | Wind - wires slap/pole down | 0 | LLC
| 352 | 2006-12-27 13:56 | Weather | Wind - wires slap/pole down | 0 | LLC
| 352 | 2006-12-27 15:07 | Weather | Wind - wires slap/pole down | 0 | LLC
| 352 | 2007-10-31 10:10 | Equipment | Conductor failure/wire down | 0 | LLC
| 352 | 2007-12-04 15:57 | Undetermined | Undetermined | 0 | LLC
| 352 | 2008-03-02 08:39 | Customer Contact | Line fault/tree trimming | 0 | LLC
| 352 | 2008-05-02 00:38 | Foreign Object | Damage by gunshot | 0 | LLC
| 352 | 2009-06-03 11:59 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 352 | 2009-10-08 09:14 | Foreign Object | Bird contact | 0 | LLC
| 352 | 2010-01-21 23:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 352 | 2010-05-19 10:15 | Tree Contact | Tree fell on line | 0 | LLC
| 352 | 2010-07-15 18:00 | Weather | Lightning Arrester/Transformer failure | 1 | LLC
| 352 | 2012-06-12 03:12 | Foreign Object | Bird contact | 0 | LLC
| 352 | 2012-09-09 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 352 | 2012-12-13 23:36 | Customer Contact | Vehicle contact | 0 | LLC
| 352 | 2013-07-21 16:05 | Customer Contact | Vehicle contact | 0 | LLC
| 352 | 2013-11-10 11:18 | Equipment | Hardware failure | 0 | LLC
| 352 | 2014-02-15 10:17 | Undetermined | Undetermined | 0 | LLC
| 352 | 2015-01-19 22:03 | Undetermined | Undetermined | 0 | LLC
| 353 | 2005-09-20 05:27 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 353 | 2005-09-20 12:05 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 353 | 2006-04-05 05:53 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 353 | 2006-05-28 06:19 | Tree Contact | Tree fell on line | 0 | LLC
| 353 | 2006-07-09 19:08 | Equipment | Conductor failure/wire down | 1 | LLC
| 353 | 2006-10-13 19:54 | Equipment | Crossarm failure | 0 | LLC
| 353 | 2009-07-30 12:09 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 353 | 2009-10-28 10:20 | Weather | Wind - wires slap/pole down | 0 | LLC
| 353 | 2009-10-28 16:51 | Weather | Wind - wires slap/pole down | 0 | LLC
| 353 | 2009-11-28 11:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 353 | 2010-01-21 13:23 | Weather | Wind - wires slap/pole down | 0 | LLC
| 353 | 2010-05-26 11:33 | Foreign Object | Bird contact | 0 | LLC
| 353 | 2010-06-17 13:03 | Foreign Object | Bird contact | 0 | LLC
| 353 | 2010-10-06 04:22 | Equipment | Insulator/pin failure/wire floating | 0 | LLC
| 353 | 2011-09-06 21:35 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 353 | 2012-08-04 14:47 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 353 | 2012-09-09 16:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 353 | 2012-09-10 05:17 | Undetermined | Undetermined | 0 | LLC
| 353 | 2012-12-13 12:42 | Equipment | Crossarm failure | 0 | LLC
| 353 | 2012-12-13 12:48 | Equipment | Crossarm failure | 0 | LLC
| 353 | 2013-07-19 10:00 | Foreign Object | Damage by gunshot | 0 | LLC
| 353 | 2013-08-18 12:54 | Foreign Object | Bird contact | 0 | LLC
| 353 | 2013-10-09 22:19 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 353 | 2013-12-09 07:06 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 353 | 2014-02-28 10:34 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 353 | 2014-03-09 08:39 | Foreign Object | Damage by gunshot | 0 | LLC
| 353 | 2014-03-25 10:27 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 353 | 2014-05-14 08:13 | Weather | Wind - wires slap/pole down | 0 | LLC
| 353 | 2014-05-15 16:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 353 | 2014-07-24 17:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 353 | 2014-11-01 03:59 | Weather | Tree fell on line due to storm/wind | 0 | LLC
| 354 | 2005-02-24 19:46 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2005-07-23 06:05 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2005-09-20 02:12 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2005-10-17 11:48 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2005-12-07 07:56 | Undetermined | Undetermined | 0 | LLC
| 354 | 2006-03-26 14:38 | Undetermined | Undetermined | 0 | LLC
| 354 | 2006-05-10 19:20 | Customer Contact | Heavy equp contact/digin | 0 | LLC
| 354 | 2006-06-19 12:49 | Customer Contact | Line fault/tree trimming | 0 | LLC
| 354 | 2006-10-14 01:23 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2006-12-03 10:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 354 | 2007-03-08 16:40 | Undetermined | Undetermined | 0 | LLC
| 354 | 2008-03-13 06:46 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 354 | 2008-03-13 11:13 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 354 | 2008-08-09 23:51 | Customer Contact | Vehicle contact | 0 | LLC
| 354 | 2008-11-26 05:42 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 354 | 2009-01-13 13:10 | Undetermined | Undetermined | 0 | LLC
| 354 | 2009-03-19 18:11 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 354 | 2009-06-03 10:03 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2009-12-07 14:42 | Weather | Wind - wires slap/pole down | 0 | LLC
| 354 | 2010-01-19 04:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC
| 354 | 2010-01-21 16:38 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2010-08-13 13:02 | Undetermined | Undetermined | 0 | LLC
| 354 | 2010-08-26 10:49 | Foreign Object | Bird contact | 0 | LLC
| 354 | 2010-11-27 07:30 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 354 | 2010-12-22 03:47 | Weather | Ice or snow/Equipment failure | 0 | LLC
| 354 | 2011-01-27 07:30 | Undetermined | Undetermined | 0 | LLC
| 354 | 2011-10-03 06:55 | Equipment | Arrester (lightning) failure | 0 | LLC
| 354 | 2011-10-18 14:40 | Customer Contact | Vehicle contact | 0 | LLC
| 354 | 2011-11-12 02:03 | Equipment | Cutout failure | 0 | LLC
| 354 | 2011-12-04 19:52 | Foreign Object | Foreign object in distribution line | 0 | LLC
| 354 | 2012-05-23 12:36 | Equipment | Arrester (lightning) failure | 0 | LLC
| 354 | 2012-09-09 16:14 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2012-10-05 10:31 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 354 | 2012-10-05 16:04 | Undetermined | Undetermined | 0 | LLC
| 354 | 2012-10-29 12:30 | Customer Contact | Heavy equp contact/digin | 0 | LLC
| 354 | 2012-10-30 07:13 | Undetermined | Undetermined | 0 | LLC
| 354 | 2012-12-20 01:24 | Undetermined | Undetermined | 0 | LLC
| 354 | 2012-12-20 07:06 | Undetermined | Undetermined | 0 | LLC
| 354 | 2013-01-11 07:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 354 | 2013-10-09 21:13 | Equipment | Transformer faulted/mechanical | 0 | LLC
| 354 | 2014-02-16 13:40 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC
| 354 | 2014-03-05 09:49 | Undetermined | Undetermined | 0 | LLC
| 354 | 2014-06-14 11:08 | Undetermined | Undetermined | 0 | LLC
| 354 | 2014-08-20 06:42 | Weather | Lightning Arrester/Transformer failure | 0 | LLC
| 354 | 2014-08-21 15:09 | Undetermined | Undetermined | 0 | LLC
| 355 | 2005-02-04 09:31 | Equipment | Insulator/pin failure/wire floating | 0 | ANE
| 355 | 2005-05-16 05:40 | Foreign Object | Bird contact | 0 | ANE
| 355 | 2007-04-13 11:20 | Customer Contact | Heavy equp contact/digin | 0 | ANE
| 355 | 2007-09-02 02:34 | Customer Contact | Vehicle contact | 0 | ANE
| 355 | 2007-10-21 21:15 | Customer Contact | Vehicle contact | 0 | ANE
| 355 | 2007-10-22 23:50 | Customer Contact | Vehicle contact | 0 | ANE
| 355 | 2007-10-22 23:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 355 | 2010-08-22 04:26 | Customer Contact | Vehicle contact | 0 | ANE
| 355 | 2010-10-19 15:56 | Weather | Lightning Arrester/Transformer failure | 0 | ANE
| 355 | 2012-04-20 16:15 | Equipment | Transformer faulted/mechanical | 0 | ANE
| 355 | 2012-09-28 11:52 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ANE
| 355 | 2012-11-06 09:11 | Undetermined | Undetermined | 0 | ANE
| 355 | 2012-12-13 02:12 | Weather | Wind - wires slap/pole down | 0 | ANE
| 355 | 2013-06-22 21:50 | Equipment | Cutout failure | 0 | ANE
| 355 | 2014-11-02 01:41 | Customer Contact | Vehicle contact | 0 | ANE
| 355 | 2014-12-03 10:01 | Undetermined | Undetermined | 0 | ANE
| 356 | 2005-01-04 19:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2005-03-20 07:45 | Tree Contact | Tree contact | 0 | WAL
| 356 | 2006-02-08 12:31 | Undetermined | Undetermined | 0 | WAL
| 356 | 2006-02-08 16:16 | Customer Contact | Vehicle contact | 0 | WAL
| 356 | 2006-02-24 22:11 | Customer Contact | Vehicle contact | 0 | WAL
| 356 | 2006-07-07 16:33 | Undetermined | Undetermined | 1 | WAL
| 356 | 2006-08-30 05:00 | Customer Contact | Vehicle contact | 0 | WAL
| 356 | 2006-09-03 14:37 | Weather | Lightning Arrester/Transformer failure | 0 | WAL
| 356 | 2007-07-04 00:05 | Customer Contact | Vehicle contact | 1 | WAL
| 356 | 2007-10-22 16:00 | Weather | Wind - wires slap/pole down | 0 | WAL
| 356 | 2007-11-01 17:58 | Customer Contact | Vehicle contact | 0 | WAL
| 356 | 2008-02-14 14:06 | Weather | Lightning Arrester/Transformer failure | 0 | WAL
| 356 | 2009-03-09 19:23 | Customer Contact | Vehicle contact | 0 | WAL
| 356 | 2009-04-11 14:45 | Undetermined | Undetermined | 0 | WAL
| 356 | 2009-09-23 10:04 | Tree Contact | Tree fell on line | 0 | WAL
| 356 | 2009-10-28 16:36 | Undetermined | Undetermined | 0 | WAL
| 356 | 2009-12-07 17:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2009-12-22 06:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2010-01-19 16:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2010-01-20 18:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2010-03-09 12:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2010-03-09 12:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL
| 356 | 2010-04-12 15:44 | Undetermined | Undetermined | 0 | WAL
| 356 | 2010-04-21 19:02 | Undetermined | Undetermined | 0 | WAL
| 356 | 2010-07-15 17:01 | Weather | Lightning Arrester/Transformer failure | 1 | WAL
| 356 | 2010-08-11 20:25 | Equipment | Pole broke/rotted/on fire | 0 | WAL
| 356 | 2010-08-24 19:12 | Equipment | Crossarm failure | 0 | WAL
| 356 | 2010-09-22 16:16 | Undetermined | Undetermined | 0 | WAL
| 356 | 2010-12-19 10:01 | Foreign Object | Bird contact | 0 | WAL
| 356 | 2011-05-21 09:03 | Undetermined | Undetermined | 0 | WAL
| 356 | 2012-03-17 14:17 | Weather | Tree fell on line due to storm/wind | 0 | WAL
| 356 | 2012-03-18 15:49 | Weather | Tree fell on line due to storm/wind | 0 | WAL
| 356 | 2012-07-11 13:37 | Foreign Object | Bird contact | 1 | WAL
| 356 | 2012-09-02 16:44 | Undetermined | Undetermined | 0 | WAL
| 356 | 2012-12-14 08:00 | Customer Contact | Vehicle contact | 0 | WAL
| 356 | 2013-04-18 16:57 | Undetermined | Undetermined | 0 | WAL
| 356 | 2013-06-19 23:11 | Undetermined | Undetermined | 0 | WAL
| 356 | 2013-06-23 14:28 | Equipment | Conductor failure/wire down | 0 | WAL
| 356 | 2013-06-24 08:50 | Foreign Object | Bird contact | 0 | WAL
| 356 | 2014-09-15 10:49 | Customer Contact | Heavy equp contact/digin | 0 | WAL
| 356 | 2014-12-02 19:52 | Undetermined | Undetermined | 0 | WAL
| 356 | 2015-02-21 06:40 | Undetermined | Undetermined | 0 | WAL
| 357 | 2005-02-17 18:17 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2005-04-28 12:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD
| 357 | 2006-01-02 14:33 | Weather | Lightning Arrester/Transformer failure | 0 | PVD
| 357 | 2006-07-23 14:48 | Equipment | Fuse overloaded/inadequate fuse size | 0 | PVD
| 357 | 2006-07-28 18:26 | Foreign Object | Foreign object in distribution line | 0 | PVD
| 357 | 2007-01-30 19:52 | Undetermined | Undetermined | 0 | PVD
| 357 | 2007-03-02 16:34 | Undetermined | Undetermined | 0 | PVD
| 357 | 2007-05-15 12:43 | Undetermined | Undetermined | 0 | PVD
| 357 | 2007-07-24 17:02 | Equipment | Fuse overloaded/inadequate fuse size | 0 | PVD
| 357 | 2007-07-28 15:23 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2007-10-22 07:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PVD
| 357 | 2007-12-12 14:59 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2008-01-27 09:21 | Weather | Tree fell on line due to storm/wind | 0 | PVD
| 357 | 2008-06-20 17:36 | Equipment | Recloser/breaker faulted/mechanical | 0 | PVD
| 357 | 2008-06-30 23:09 | Foreign Object | Bird contact | 0 | PVD
| 357 | 2008-11-09 11:40 | Undetermined | Undetermined | 0 | PVD
| 357 | 2009-08-25 14:11 | Tree Contact | Tree fell on line | 0 | PVD
| 357 | 2009-10-06 10:18 | Undetermined | Undetermined | 0 | PVD
| 357 | 2009-11-26 10:54 | Undetermined | Undetermined | 0 | PVD
| 357 | 2009-12-07 15:26 | Weather | Tree fell on line due to storm/wind | 0 | PVD
| 357 | 2009-12-07 16:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD
| 357 | 2010-02-21 12:17 | Foreign Object | Flashover/vegetation | 0 | PVD
| 357 | 2010-07-15 17:07 | Weather | Lightning Arrester/Transformer failure | 1 | PVD
| 357 | 2010-08-21 21:28 | Equipment | Cutout failure | 0 | PVD
| 357 | 2010-09-30 17:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD
| 357 | 2010-10-17 15:15 | Undetermined | Undetermined | 0 | PVD
| 357 | 2011-01-15 19:43 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2011-02-27 15:02 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2011-07-19 08:51 | Equipment | Arrester (lightning) failure | 0 | PVD
| 357 | 2011-07-30 06:10 | Undetermined | Undetermined | 0 | PVD
| 357 | 2011-08-12 12:13 | Foreign Object | Bird contact | 0 | PVD
| 357 | 2011-10-14 08:11 | Undetermined | Undetermined | 0 | PVD
| 357 | 2012-02-26 12:04 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2012-04-14 10:51 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2012-04-25 13:09 | Foreign Object | Foreign object in distribution line | 0 | PVD
| 357 | 2012-05-24 18:55 | Undetermined | Undetermined | 0 | PVD
| 357 | 2013-05-07 03:41 | Undetermined | Undetermined | 0 | PVD
| 357 | 2013-05-20 16:29 | Equipment | Cutout failure | 0 | PVD
| 357 | 2014-03-01 17:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD
| 357 | 2014-03-27 02:05 | Weather | Lightning Arrester/Transformer failure | 0 | PVD
| 357 | 2014-04-30 06:17 | Weather | Tree fell on line due to storm/wind | 0 | PVD
| 357 | 2014-05-16 02:33 | Foreign Object | Bird contact | 0 | PVD
| 357 | 2014-06-29 04:54 | Undetermined | Undetermined | 0 | PVD
| 357 | 2014-12-02 20:40 | Undetermined | Undetermined | 0 | PVD
| 357 | 2014-12-03 19:58 | Equipment | Arrester (lightning) failure | 0 | PVD
| 357 | 2015-02-27 13:00 | Customer Contact | Vehicle contact | 0 | PVD
| 357 | 2015-03-02 00:29 | Equipment | Arrester (lightning) failure | 0 | PVD
| 357 | 2015-03-13 12:30 | Undetermined | Undetermined | 0 | PVD
| 358 | 2005-01-12 12:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 358 | 2005-02-17 18:17 | Customer Contact | Vehicle contact | 0 | ANE
| 358 | 2005-07-14 10:36 | Equipment | Arrester (lightning) failure | 1 | ANE
| 358 | 2005-07-31 12:01 | Weather | Lightning Arrester/Transformer failure | 0 | ANE
| 358 | 2005-08-17 13:56 | Equipment | Arrester (lightning) failure | 0 | ANE
| 358 | 2005-10-21 10:49 | Equipment | Crossarm failure | 0 | ANE
| 358 | 2006-03-11 15:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 358 | 2006-11-29 17:29 | Weather | Wind - wires slap/pole down | 0 | ANE
| 358 | 2007-05-22 08:01 | Foreign Object | Bird contact | 0 | ANE
| 358 | 2007-08-23 07:40 | Customer Contact | Vehicle contact | 0 | ANE
| 358 | 2007-10-21 21:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 358 | 2007-10-22 06:41 | Weather | Wind - wires slap/pole down | 0 | ANE
| 358 | 2007-11-30 15:44 | Weather | Wind - wires slap/pole down | 0 | ANE
| 358 | 2008-10-14 09:52 | Equipment | Crossarm failure | 0 | ANE
| 358 | 2009-01-11 23:13 | Undetermined | Undetermined | 0 | ANE
| 358 | 2009-07-02 22:21 | Customer Contact | Vehicle contact | 1 | ANE
| 358 | 2009-11-28 09:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 358 | 2010-07-15 17:32 | Weather | Lightning Arrester/Transformer failure | 1 | ANE
| 358 | 2010-10-19 19:55 | Weather | Lightning Arrester/Transformer failure | 0 | ANE
| 358 | 2010-10-26 09:46 | Undetermined | Undetermined | 0 | ANE
| 358 | 2010-12-23 23:15 | Weather | Wind - wires slap/pole down | 0 | ANE
| 358 | 2011-05-06 16:17 | Foreign Object | Foreign object in distribution line | 0 | ANE
| 358 | 2011-07-30 07:59 | Foreign Object | Foreign object in distribution line | 0 | ANE
| 358 | 2011-12-09 15:49 | Undetermined | Undetermined | 0 | ANE
| 358 | 2012-07-21 21:31 | Foreign Object | Foreign object in distribution line | 0 | ANE
| 358 | 2012-10-11 12:40 | Equipment | Fuse overloaded/inadequate fuse size | 0 | ANE
| 358 | 2013-07-21 17:05 | Equipment | Transformer faulted/mechanical | 0 | ANE
| 358 | 2014-05-14 08:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE
| 374 | 2005-10-12 19:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | KSAN
| 374 | 2006-08-05 18:48 | Undetermined | Undetermined | 0 | KSAN
| 374 | 2007-04-24 14:39 | Equipment | Crossarm failure | 0 | KSAN
| 374 | 2008-10-04 20:44 | Equipment | Cutout failure | 0 | KSAN
| 374 | 2010-04-18 10:48 | Undetermined | Undetermined | 0 | KSAN
| 374 | 2012-09-16 05:45 | Equipment | Transformer faulted/mechanical | 0 | KSAN
| 374 | 2013-03-31 14:28 | Foreign Object | Foreign object in distribution line | 0 | KSAN
| 374 | 2013-06-09 17:59 | Undetermined | Undetermined | 0 | KSAN
| 374 | 2014-05-17 06:40 | Customer Contact | Vehicle contact | 0 | KSAN
| 374 | 2014-06-04 09:29 | Undetermined | Undetermined | 0 | KSAN
| 378 | 2011-04-10 17:12 | Undetermined | Undetermined | 0 | KSAN
| 378 | 2014-12-02 23:20 | Customer Contact | Vehicle contact | 0 | KSAN
| 411 | 2005-06-06 07:16 | Foreign Object | Bird contact | 0 | cst
| 411 | 2005-09-20 09:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst
| 411 | 2005-09-20 12:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst
| 411 | 2005-10-05 15:57 | Undetermined | Undetermined | 0 | cst
| 411 | 2006-02-06 13:20 | Equipment | Arrester (lightning) failure | 0 | cst
| 411 | 2006-03-11 12:37 | Weather | Lightning Arrester/Transformer failure | 0 | cst
| 411 | 2007-04-14 23:31 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2007-10-23 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst
| 411 | 2008-05-25 17:49 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2008-07-09 19:23 | Equipment | Connector/jumper/splice/elbow/rack | 1 | cst
| 411 | 2009-01-29 15:18 | Equipment | Conductor contact/wire slap | 0 | cst
| 411 | 2009-02-12 21:45 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2009-12-07 17:36 | Weather | Wind - wires slap/pole down | 0 | cst
| 411 | 2010-01-19 15:03 | Weather | Wind - wires slap/pole down | 0 | cst
| 411 | 2010-01-20 08:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst
| 411 | 2010-01-21 06:51 | Weather | Wind - wires slap/pole down | 0 | cst
| 411 | 2010-01-21 13:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst
| 411 | 2010-02-10 11:11 | Tree Contact | Palm frond contact | 0 | cst
| 411 | 2010-02-28 10:56 | Tree Contact | Tree fell on line | 0 | cst
| 411 | 2010-09-30 13:10 | Weather | Lightning Arrester/Transformer failure | 0 | cst
| 411 | 2010-09-30 13:10 | Weather | Lightning Arrester/Transformer failure | 0 | cst
| 411 | 2010-10-01 10:00 | Weather | Lightning Arrester/Transformer failure | 0 | cst
| 411 | 2010-12-22 01:55 | Weather | Ice or snow/Equipment failure | 0 | cst
| 411 | 2011-07-28 13:09 | Undetermined | Undetermined | 0 | cst
| 411 | 2011-08-13 08:56 | Equipment | Arrester (lightning) failure | 0 | cst
| 411 | 2011-10-06 09:55 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2012-02-25 12:59 | Foreign Object | Foreign object in distribution line | 0 | cst
| 411 | 2012-05-07 16:17 | Equipment | Transformer faulted/mechanical | 0 | cst
| 411 | 2012-06-09 12:40 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2012-06-09 13:50 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2012-07-16 05:33 | Foreign Object | Bird contact | 0 | cst
| 411 | 2012-12-27 20:44 | Equipment | Guy wire failure | 0 | cst
| 411 | 2013-01-25 06:08 | Foreign Object | Flashover/vegetation | 0 | cst
| 411 | 2013-05-05 23:26 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2013-06-11 09:27 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2013-09-15 17:44 | Undetermined | Undetermined | 0 | cst
| 411 | 2013-11-21 07:33 | Weather | Circuit Flashover/fog/foreign object | 0 | cst
| 411 | 2014-06-09 18:31 | Foreign Object | Bird contact | 0 | cst
| 411 | 2014-08-04 18:40 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2014-10-11 03:40 | Customer Contact | Vehicle contact | 0 | cst
| 411 | 2015-02-01 08:50 | Foreign Object | Bird contact | 0 | cst
| 440 | 2005-02-17 09:27 | Undetermined | Undetermined | 0 | LAG
| 440 | 2005-08-04 17:35 | Weather | Lightning Arrester/Transformer failure | 0 | LAG
| 440 | 2005-08-11 12:20 | Undetermined | Undetermined | 0 | LAG
| 440 | 2006-01-05 20:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG
| 440 | 2007-03-08 08:44 | Undetermined | Undetermined | 0 | LAG
| 440 | 2007-08-01 12:45 | Undetermined | Undetermined | 0 | LAG
| 440 | 2007-11-15 13:08 | Equipment | Pole broke/rotted/on fire | 0 | LAG
| 440 | 2008-01-06 13:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG
| 440 | 2008-12-13 20:31 | Weather | Wind - wires slap/pole down | 0 | LAG
| 440 | 2009-02-05 22:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG
| 440 | 2009-12-06 17:55 | Undetermined | Undetermined | 0 | LAG
| 440 | 2009-12-08 03:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG
| 440 | 2010-08-26 08:49 | Undetermined | Undetermined | 0 | LAG
| 440 | 2010-10-01 13:43 | Equipment | Regulator faulted/mechanical | 0 | LAG
| 440 | 2011-02-20 07:57 | Weather | Tree fell on line due to storm/wind | 0 | LAG
| 440 | 2011-04-13 14:40 | Undetermined | Undetermined | 0 | LAG
| 440 | 2011-07-08 19:12 | Undetermined | Undetermined | 1 | LAG
| 440 | 2011-07-16 16:16 | Foreign Object | Bird contact | 0 | LAG
| 440 | 2011-09-21 08:48 | Foreign Object | Animal contact | 0 | LAG
| 440 | 2011-09-22 08:29 | Foreign Object | Animal contact | 0 | LAG
| 440 | 2011-12-03 10:29 | Undetermined | Undetermined | 0 | LAG
| 440 | 2012-07-13 07:12 | Foreign Object | Animal contact | 1 | LAG
| 440 | 2012-07-24 07:20 | Foreign Object | Animal contact | 0 | LAG
| 440 | 2012-10-18 16:25 | Undetermined | Undetermined | 0 | LAG
| 440 | 2012-12-14 04:58 | Undetermined | Undetermined | 0 | LAG
| 440 | 2012-12-14 09:05 | Undetermined | Undetermined | 0 | LAG
| 440 | 2013-02-15 23:07 | Undetermined | Undetermined | 0 | LAG
| 440 | 2013-02-16 02:02 | Undetermined | Undetermined | 0 | LAG
| 440 | 2013-07-25 11:24 | Foreign Object | Bird contact | 0 | LAG
| 440 | 2013-07-25 14:10 | Foreign Object | Bird contact | 0 | LAG
| 440 | 2013-08-27 15:20 | Undetermined | Undetermined | 0 | LAG
| 440 | 2013-08-29 08:40 | Weather | Lightning Arrester/Transformer failure | 0 | LAG
| 440 | 2013-09-03 16:12 | Weather | Lightning Arrester/Transformer failure | 0 | LAG
| 440 | 2013-09-03 16:12 | Weather | Lightning Arrester/Transformer failure | 0 | LAG
| 440 | 2013-09-06 13:58 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LAG
| 440 | 2013-09-10 18:46 | Undetermined | Undetermined | 0 | LAG
| 440 | 2013-12-07 15:22 | Weather | Ice or snow/Equipment failure | 0 | LAG
| 440 | 2014-05-01 09:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG
| 440 | 2014-07-07 19:01 | Undetermined | Undetermined | 1 | LAG
| 440 | 2014-07-08 12:29 | Equipment | Transformer faulted/mechanical | 1 | LAG
| 440 | 2014-07-09 12:51 | Equipment | Pole broke/rotted/on fire | 1 | LAG
| 440 | 2014-07-15 01:13 | Equipment | Cutout failure | 1 | LAG
| 441 | 2005-07-26 08:48 | Weather | Lightning Arrester/Transformer failure | 0 | LPT
| 441 | 2005-11-01 10:40 | Foreign Object | Bird contact | 0 | LPT
| 441 | 2006-01-31 08:28 | Equipment | Arrester (lightning) failure | 0 | LPT
| 441 | 2006-03-11 13:22 | Weather | Wind - wires slap/pole down | 0 | LPT
| 441 | 2007-03-03 13:13 | Weather | Wind - wires slap/pole down | 0 | LPT
| 441 | 2007-04-28 03:07 | Customer Contact | Vehicle contact | 0 | LPT
| 441 | 2007-10-22 02:39 | Weather | Wind - wires slap/pole down | 0 | LPT
| 441 | 2007-11-09 23:12 | Weather | Wind - wires slap/pole down | 0 | LPT
| 441 | 2008-05-12 08:44 | Equipment | Capacitor failure | 0 | LPT
| 441 | 2008-06-30 12:40 | Foreign Object | Bird contact | 0 | LPT
| 441 | 2009-03-24 06:45 | Undetermined | Undetermined | 0 | LPT
| 441 | 2009-08-27 10:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LPT
| 441 | 2010-04-07 06:35 | Tree Contact | Tree fell on line | 0 | LPT
| 441 | 2011-02-02 08:02 | Weather | Circuit Flashover/fog/foreign object | 0 | LPT
| 441 | 2011-05-24 08:17 | Undetermined | Undetermined | 0 | LPT
| 441 | 2011-05-26 02:41 | Undetermined | Undetermined | 0 | LPT
| 441 | 2011-05-26 13:45 | Undetermined | Undetermined | 0 | LPT
| 441 | 2012-02-27 21:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LPT
| 441 | 2012-02-27 22:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LPT
| 441 | 2012-08-13 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LPT
| 441 | 2013-02-20 01:19 | Weather | Ice or snow/Equipment failure | 0 | LPT
| 441 | 2013-07-20 17:01 | Undetermined | Undetermined | 0 | LPT
| 441 | 2013-09-07 13:29 | Weather | Lightning Arrester/Transformer failure | 0 | LPT
| 441 | 2014-08-02 08:40 | Undetermined | Undetermined | 0 | LPT
| 442 | 2005-08-06 15:49 | Weather | Lightning Arrester/Transformer failure | 0 | SRH
| 442 | 2005-10-04 14:04 | Foreign Object | Animal contact | 0 | SRH
| 442 | 2006-03-11 09:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2006-03-12 10:45 | Weather | Ice or snow/Equipment failure | 0 | SRH
| 442 | 2006-04-27 03:16 | Equipment | Transformer faulted/mechanical | 0 | SRH
| 442 | 2006-10-20 08:20 | Equipment | Cutout failure | 0 | SRH
| 442 | 2007-05-01 11:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2007-05-01 11:53 | Weather | Lightning Arrester/Transformer failure | 0 | SRH
| 442 | 2007-07-19 09:44 | Undetermined | Undetermined | 0 | SRH
| 442 | 2007-09-02 10:56 | Weather | Lightning Arrester/Transformer failure | 0 | SRH
| 442 | 2007-09-13 08:01 | Foreign Object | Animal contact | 0 | SRH
| 442 | 2007-10-22 00:11 | Weather | Wind - wires slap/pole down | 0 | SRH
| 442 | 2007-10-22 01:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2007-10-22 17:07 | Weather | Wind - wires slap/pole down | 0 | SRH
| 442 | 2008-01-14 07:36 | Undetermined | Undetermined | 0 | SRH
| 442 | 2008-02-03 13:46 | Undetermined | Undetermined | 0 | SRH
| 442 | 2008-02-03 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2008-02-03 16:34 | Weather | Lightning Arrester/Transformer failure | 0 | SRH
| 442 | 2008-07-13 09:11 | Undetermined | Undetermined | 1 | SRH
| 442 | 2009-01-10 21:02 | Weather | Wind - wires slap/pole down | 0 | SRH
| 442 | 2009-12-08 00:51 | Weather | Wind - wires slap/pole down | 0 | SRH
| 442 | 2010-07-30 06:46 | Foreign Object | Bird contact | 0 | SRH
| 442 | 2010-08-09 11:15 | Undetermined | Undetermined | 0 | SRH
| 442 | 2010-09-19 04:33 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SRH
| 442 | 2011-01-31 06:20 | Undetermined | Undetermined | 0 | SRH
| 442 | 2011-07-05 18:27 | Undetermined | Undetermined | 1 | SRH
| 442 | 2011-07-06 17:15 | Weather | Lightning Arrester/Transformer failure | 1 | SRH
| 442 | 2011-07-18 12:19 | Foreign Object | Bird contact | 0 | SRH
| 442 | 2011-08-27 13:01 | Undetermined | Undetermined | 0 | SRH
| 442 | 2012-02-14 09:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2012-02-28 00:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2012-02-28 02:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2012-02-28 02:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2012-02-28 03:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2012-03-18 05:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2012-03-18 12:24 | Weather | Wind - wires slap/pole down | 0 | SRH
| 442 | 2012-05-15 18:24 | Customer Contact | Heavy equp contact/digin | 0 | SRH
| 442 | 2012-06-09 17:53 | Foreign Object | Bird contact | 0 | SRH
| 442 | 2012-08-07 12:43 | Weather | Lightning Arrester/Transformer failure | 0 | SRH
| 442 | 2012-10-18 09:46 | Foreign Object | Animal contact | 0 | SRH
| 442 | 2013-07-21 13:59 | Undetermined | Undetermined | 0 | SRH
| 442 | 2013-09-05 14:00 | Weather | Tree fell on line due to storm/wind | 0 | SRH
| 442 | 2013-09-05 14:52 | Weather | Lightning Arrester/Transformer failure | 0 | SRH
| 442 | 2014-03-24 09:49 | Customer Contact | Vehicle contact | 0 | SRH
| 442 | 2014-04-30 06:11 | Weather | Tree fell on line due to storm/wind | 0 | SRH
| 442 | 2014-05-01 04:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH
| 442 | 2015-02-11 14:30 | Equipment | Conductor failure/wire down | 0 | SRH
| 444 | 2005-01-02 12:50 | Foreign Object | Animal contact | 0 | BVD
| 444 | 2005-02-22 07:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 444 | 2005-04-09 00:29 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2005-07-21 17:32 | Undetermined | Undetermined | 0 | BVD
| 444 | 2005-07-22 14:34 | Undetermined | Undetermined | 0 | BVD
| 444 | 2005-10-19 09:31 | Equipment | Transformer faulted/mechanical | 0 | BVD
| 444 | 2006-10-06 06:04 | Undetermined | Undetermined | 0 | BVD
| 444 | 2007-01-11 20:50 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2007-01-12 09:00 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2007-03-02 19:57 | Undetermined | Undetermined | 0 | BVD
| 444 | 2007-06-16 14:48 | Undetermined | Undetermined | 0 | BVD
| 444 | 2008-03-16 07:52 | Weather | Ice or snow/Equipment failure | 0 | BVD
| 444 | 2008-05-20 11:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 444 | 2008-05-20 13:50 | Equipment | Insulator/pin failure/wire floating | 0 | BVD
| 444 | 2008-11-30 05:02 | Equipment | Transformer faulted/mechanical | 0 | BVD
| 444 | 2008-12-13 17:40 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2009-05-29 19:55 | Undetermined | Undetermined | 0 | BVD
| 444 | 2009-06-29 14:16 | Undetermined | Undetermined | 0 | BVD
| 444 | 2009-08-26 15:50 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD
| 444 | 2009-12-07 20:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 444 | 2009-12-27 03:19 | Equipment | Conductor failure/wire down | 0 | BVD
| 444 | 2010-01-20 11:23 | Equipment | Transformer faulted/mechanical | 0 | BVD
| 444 | 2010-02-19 07:03 | Customer Contact | Heavy equp contact/digin | 0 | BVD
| 444 | 2010-03-07 12:02 | Customer Contact | Vehicle contact | 0 | BVD
| 444 | 2010-03-20 01:11 | Equipment | Conductor failure/wire down | 0 | BVD
| 444 | 2010-06-18 11:40 | Undetermined | Undetermined | 0 | BVD
| 444 | 2010-09-27 09:27 | Undetermined | Undetermined | 0 | BVD
| 444 | 2010-10-02 02:42 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 444 | 2010-10-02 10:52 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 444 | 2010-10-03 03:39 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 444 | 2010-10-04 09:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 444 | 2011-01-11 17:50 | Undetermined | Undetermined | 0 | BVD
| 444 | 2011-03-08 15:55 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2011-07-05 08:53 | Foreign Object | Bird contact | 1 | BVD
| 444 | 2011-08-28 18:11 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 444 | 2011-10-12 00:44 | Undetermined | Undetermined | 0 | BVD
| 444 | 2012-02-27 22:05 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2012-03-07 07:19 | Equipment | Cutout failure | 0 | BVD
| 444 | 2012-03-18 22:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 444 | 2012-03-19 14:17 | Weather | Wind - wires slap/pole down | 0 | BVD
| 444 | 2012-03-25 22:59 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD
| 444 | 2012-06-16 14:19 | Foreign Object | Bird contact | 0 | BVD
| 444 | 2012-07-17 22:29 | Equipment | Conductor failure/wire down | 0 | BVD
| 444 | 2012-08-13 18:37 | Equipment | Insulator/pin failure/wire floating | 0 | BVD
| 444 | 2012-08-13 20:50 | Equipment | Transformer overloaded/electrical | 0 | BVD
| 444 | 2012-08-21 14:07 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 444 | 2012-11-08 02:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD
| 444 | 2012-11-13 10:38 | Undetermined | Undetermined | 0 | BVD
| 444 | 2013-02-08 22:54 | Weather | Ice or snow/Equipment failure | 0 | BVD
| 444 | 2013-03-28 14:02 | Foreign Object | Flashover/vegetation | 0 | BVD
| 444 | 2013-06-03 17:02 | Undetermined | Undetermined | 0 | BVD
| 444 | 2013-07-20 17:52 | Undetermined | Undetermined | 0 | BVD
| 444 | 2013-07-21 15:40 | Equipment | Fuse holder/fuse cabinet failed | 0 | BVD
| 444 | 2013-09-13 04:23 | Equipment | Hardware failure | 0 | BVD
| 444 | 2013-10-31 14:38 | Foreign Object | Bird contact | 0 | BVD
| 444 | 2013-11-06 08:16 | Equipment | Fuse overloaded/inadequate fuse size | 0 | BVD
| 444 | 2014-03-06 16:03 | Undetermined | Undetermined | 0 | BVD
| 444 | 2014-03-10 07:12 | Undetermined | Undetermined | 0 | BVD
| 444 | 2014-04-09 10:51 | Undetermined | Undetermined | 0 | BVD
| 444 | 2014-04-19 16:26 | Undetermined | Undetermined | 0 | BVD
| 444 | 2014-08-02 16:04 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 444 | 2014-11-19 00:07 | Weather | Ice or snow/Equipment failure | 0 | BVD
| 445 | 2005-02-05 16:53 | Undetermined | Undetermined | 0 | BVD
| 445 | 2005-02-08 01:20 | Customer Contact | Vehicle contact | 0 | BVD
| 445 | 2005-03-23 11:31 | Equipment | Conductor failure/wire down | 0 | BVD
| 445 | 2005-04-27 13:50 | Undetermined | Undetermined | 0 | BVD
| 445 | 2005-07-24 17:23 | Undetermined | Undetermined | 0 | BVD
| 445 | 2005-07-28 20:04 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2005-08-04 15:28 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2005-08-15 09:11 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2005-09-07 10:54 | Customer Contact | Vehicle contact | 0 | BVD
| 445 | 2005-09-19 15:07 | Equipment | Regulator faulted/mechanical | 0 | BVD
| 445 | 2005-10-01 07:50 | Undetermined | Undetermined | 0 | BVD
| 445 | 2005-10-26 16:18 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2005-11-14 15:02 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2005-11-28 09:57 | Undetermined | Undetermined | 0 | BVD
| 445 | 2005-12-11 07:15 | Equipment | Conductor failure/wire down | 0 | BVD
| 445 | 2006-01-23 09:23 | Equipment | Conductor failure/wire down | 0 | BVD
| 445 | 2006-03-02 09:32 | Equipment | Recloser/breaker faulted/mechanical | 0 | BVD
| 445 | 2006-03-11 09:15 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2006-03-11 21:00 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2006-07-05 15:43 | Weather | Lightning Arrester/Transformer failure | 1 | BVD
| 445 | 2006-07-05 17:23 | Weather | Lightning Arrester/Transformer failure | 1 | BVD
| 445 | 2006-07-05 18:05 | Weather | Lightning Arrester/Transformer failure | 1 | BVD
| 445 | 2006-07-05 18:12 | Weather | Lightning Arrester/Transformer failure | 1 | BVD
| 445 | 2006-07-07 16:04 | Undetermined | Undetermined | 1 | BVD
| 445 | 2006-09-08 08:17 | Equipment | Recloser/breaker faulted/mechanical | 0 | BVD
| 445 | 2006-10-10 15:23 | Equipment | Recloser/breaker faulted/mechanical | 0 | BVD
| 445 | 2006-12-27 15:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2007-02-25 07:20 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2007-07-10 09:00 | Undetermined | Undetermined | 1 | BVD
| 445 | 2007-07-12 15:50 | Equipment | Transformer faulted/mechanical | 1 | BVD
| 445 | 2007-09-01 16:34 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2007-10-21 20:16 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2007-10-22 08:11 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2007-11-30 17:00 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD
| 445 | 2008-02-28 01:09 | Undetermined | Undetermined | 0 | BVD
| 445 | 2008-03-16 04:35 | Weather | Ice or snow/Equipment failure | 0 | BVD
| 445 | 2008-06-16 17:49 | Foreign Object | Vandalism | 0 | BVD
| 445 | 2008-07-09 11:22 | Equipment | Connector/jumper/splice/elbow/rack | 1 | BVD
| 445 | 2008-08-14 11:01 | Foreign Object | Vandalism | 0 | BVD
| 445 | 2008-12-14 08:52 | Foreign Object | Animal contact | 0 | BVD
| 445 | 2008-12-17 12:55 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2008-12-17 16:36 | Undetermined | Undetermined | 0 | BVD
| 445 | 2009-05-17 12:30 | Undetermined | Undetermined | 0 | BVD
| 445 | 2009-06-26 18:12 | Customer Contact | Line fault/tree trimming | 0 | BVD
| 445 | 2009-08-06 16:19 | Undetermined | Undetermined | 0 | BVD
| 445 | 2009-09-02 18:36 | Customer Contact | Vehicle contact | 0 | BVD
| 445 | 2009-10-08 11:21 | Equipment | Crossarm failure | 0 | BVD
| 445 | 2009-12-12 03:53 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2010-01-19 15:41 | Weather | Ice or snow/Equipment failure | 0 | BVD
| 445 | 2010-01-30 08:38 | Undetermined | Undetermined | 0 | BVD
| 445 | 2010-02-16 13:44 | Foreign Object | Foreign object in distribution line | 0 | BVD
| 445 | 2010-04-15 07:12 | Undetermined | Undetermined | 0 | BVD
| 445 | 2010-04-29 08:00 | Equipment | Arrester (lightning) failure | 0 | BVD
| 445 | 2010-06-24 10:49 | Equipment | Pole broke/rotted/on fire | 0 | BVD
| 445 | 2010-07-06 08:23 | Undetermined | Undetermined | 1 | BVD
| 445 | 2010-07-15 16:10 | Weather | Lightning Arrester/Transformer failure | 1 | BVD
| 445 | 2010-08-23 17:02 | Undetermined | Undetermined | 0 | BVD
| 445 | 2010-09-07 12:41 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2010-10-02 02:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2010-10-03 03:20 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2010-10-19 17:49 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2010-10-20 14:09 | Equipment | Cutout failure | 0 | BVD
| 445 | 2010-11-29 01:24 | Undetermined | Undetermined | 0 | BVD
| 445 | 2010-12-03 04:41 | Equipment | Transformer faulted/mechanical | 0 | BVD
| 445 | 2010-12-10 04:58 | Undetermined | Undetermined | 0 | BVD
| 445 | 2011-01-11 07:20 | Equipment | Conductor failure/wire down | 0 | BVD
| 445 | 2011-02-20 03:37 | Weather | Ice or snow/Equipment failure | 0 | BVD
| 445 | 2011-02-20 03:52 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2011-03-11 09:05 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2011-05-26 09:05 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD
| 445 | 2011-06-17 03:58 | Undetermined | Undetermined | 0 | BVD
| 445 | 2011-06-26 06:16 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2011-07-02 12:00 | Foreign Object | Bird contact | 1 | BVD
| 445 | 2011-07-05 17:18 | Undetermined | Undetermined | 1 | BVD
| 445 | 2011-07-05 17:27 | Undetermined | Undetermined | 1 | BVD
| 445 | 2011-07-05 17:53 | Weather | Lightning Arrester/Transformer failure | 1 | BVD
| 445 | 2011-07-18 10:28 | Undetermined | Undetermined | 0 | BVD
| 445 | 2011-07-31 12:54 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2011-09-03 12:26 | Foreign Object | Foreign object in distribution line | 0 | BVD
| 445 | 2011-09-23 18:03 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2011-09-30 16:10 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2012-02-10 04:17 | Undetermined | Undetermined | 0 | BVD
| 445 | 2012-02-14 05:35 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2012-02-18 14:01 | Undetermined | Undetermined | 0 | BVD
| 445 | 2012-02-27 19:23 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2012-02-27 20:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2012-02-27 21:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2012-02-27 21:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2012-02-27 21:34 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2012-02-28 05:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2012-03-18 18:33 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2012-03-19 08:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2012-04-10 08:48 | Undetermined | Undetermined | 0 | BVD
| 445 | 2012-04-14 19:17 | Undetermined | Undetermined | 0 | BVD
| 445 | 2012-04-17 09:20 | Undetermined | Undetermined | 0 | BVD
| 445 | 2012-04-19 07:51 | Undetermined | Undetermined | 0 | BVD
| 445 | 2012-05-08 09:22 | Equipment | Recloser/breaker overloaded/electrical | 0 | BVD
| 445 | 2012-05-20 07:28 | Equipment | Recloser/breaker overloaded/electrical | 0 | BVD
| 445 | 2012-05-20 07:56 | Equipment | Recloser/breaker overloaded/electrical | 0 | BVD
| 445 | 2012-05-28 13:30 | Customer Contact | Vehicle contact | 0 | BVD
| 445 | 2012-06-27 11:52 | Equipment | Pole broke/rotted/on fire | 0 | BVD
| 445 | 2012-08-11 14:31 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2012-08-18 15:16 | Undetermined | Undetermined | 0 | BVD
| 445 | 2013-01-08 05:19 | Foreign Object | Foreign object in distribution line | 0 | BVD
| 445 | 2013-02-20 02:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD
| 445 | 2013-03-22 08:11 | Undetermined | Undetermined | 0 | BVD
| 445 | 2013-06-26 09:25 | Foreign Object | Bird contact | 0 | BVD
| 445 | 2013-07-21 19:36 | Equipment | Transformer faulted/mechanical | 0 | BVD
| 445 | 2013-07-30 12:45 | Tree Contact | Tree fell on line | 0 | BVD
| 445 | 2013-09-20 08:24 | Undetermined | Undetermined | 0 | BVD
| 445 | 2013-12-09 11:30 | Equipment | Arrester (lightning) failure | 0 | BVD
| 445 | 2014-03-01 00:38 | Weather | Wind - wires slap/pole down | 0 | BVD
| 445 | 2014-03-04 14:37 | Undetermined | Undetermined | 0 | BVD
| 445 | 2014-03-10 08:02 | Undetermined | Undetermined | 0 | BVD
| 445 | 2014-05-06 04:29 | Equipment | Insulator/pin failure/wire floating | 0 | BVD
| 445 | 2014-05-06 07:27 | Equipment | Insulator/pin failure/wire floating | 0 | BVD
| 445 | 2014-06-09 06:34 | Undetermined | Undetermined | 0 | BVD
| 445 | 2014-06-25 22:17 | Undetermined | Undetermined | 0 | BVD
| 445 | 2014-08-12 12:48 | Weather | Lightning Arrester/Transformer failure | 0 | BVD
| 445 | 2014-08-20 15:23 | Undetermined | Undetermined | 0 | BVD
| 445 | 2014-08-27 01:45 | Undetermined | Undetermined | 0 | BVD
| 445 | 2014-11-22 05:53 | Undetermined | Undetermined | 0 | BVD
| 448 | 2005-06-25 10:16 | Equipment | Conductor failure/wire down | 0 | WPT
| 448 | 2005-07-24 20:53 | Equipment | Arrester (lightning) failure | 0 | WPT
| 448 | 2005-08-06 13:36 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2005-08-17 19:19 | Undetermined | Undetermined | 0 | WPT
| 448 | 2006-02-28 05:46 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2006-06-28 13:32 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2006-07-01 14:24 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2006-07-03 06:09 | Foreign Object | Bird contact | 1 | WPT
| 448 | 2006-07-15 15:02 | Weather | Lightning Arrester/Transformer failure | 1 | WPT
| 448 | 2006-07-15 15:08 | Weather | Lightning Arrester/Transformer failure | 1 | WPT
| 448 | 2006-07-15 17:09 | Weather | Lightning Arrester/Transformer failure | 1 | WPT
| 448 | 2006-07-20 09:09 | Customer Contact | Heavy equp contact/digin | 0 | WPT
| 448 | 2006-07-23 14:43 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2006-09-02 14:11 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2006-09-11 10:07 | Undetermined | Undetermined | 0 | WPT
| 448 | 2006-11-29 19:36 | Weather | Wind - wires slap/pole down | 0 | WPT
| 448 | 2006-12-25 19:21 | Undetermined | Undetermined | 0 | WPT
| 448 | 2007-05-30 06:21 | Undetermined | Undetermined | 0 | WPT
| 448 | 2007-06-12 15:40 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2007-08-31 00:53 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2007-09-01 15:41 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2007-10-22 09:57 | Weather | Wind - wires slap/pole down | 0 | WPT
| 448 | 2007-10-23 12:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT
| 448 | 2007-11-02 12:25 | Undetermined | Undetermined | 0 | WPT
| 448 | 2008-03-25 12:29 | Undetermined | Undetermined | 0 | WPT
| 448 | 2008-09-03 15:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT
| 448 | 2008-09-28 15:43 | Undetermined | Undetermined | 0 | WPT
| 448 | 2009-01-02 18:19 | Equipment | Transformer faulted/mechanical | 0 | WPT
| 448 | 2009-01-30 11:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WPT
| 448 | 2009-03-31 09:09 | Undetermined | Undetermined | 0 | WPT
| 448 | 2009-08-26 21:04 | Equipment | Fuse overloaded/inadequate fuse size | 0 | WPT
| 448 | 2009-11-28 01:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT
| 448 | 2010-04-06 11:02 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2010-07-03 14:00 | Undetermined | Undetermined | 1 | WPT
| 448 | 2010-10-03 04:43 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2010-11-04 09:12 | Equipment | Fuse overloaded/inadequate fuse size | 0 | WPT
| 448 | 2011-07-04 15:04 | Undetermined | Undetermined | 1 | WPT
| 448 | 2011-07-06 17:17 | Weather | Lightning Arrester/Transformer failure | 1 | WPT
| 448 | 2011-08-21 14:46 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2011-08-28 14:52 | Weather | Wind - wires slap/pole down | 0 | WPT
| 448 | 2011-10-02 16:52 | Undetermined | Undetermined | 0 | WPT
| 448 | 2011-10-11 08:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WPT
| 448 | 2011-12-02 13:24 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WPT
| 448 | 2012-01-28 12:40 | Equipment | Capacitor failure | 0 | WPT
| 448 | 2012-04-26 04:26 | Undetermined | Undetermined | 0 | WPT
| 448 | 2012-06-03 07:50 | Undetermined | Undetermined | 0 | WPT
| 448 | 2012-06-06 07:36 | Undetermined | Undetermined | 0 | WPT
| 448 | 2012-06-19 18:59 | Undetermined | Undetermined | 0 | WPT
| 448 | 2012-07-04 22:41 | Undetermined | Undetermined | 1 | WPT
| 448 | 2012-07-19 13:40 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2012-08-03 21:51 | Equipment | Conductor failure/wire down | 0 | WPT
| 448 | 2012-08-11 14:50 | Equipment | Arrester (lightning) failure | 0 | WPT
| 448 | 2012-08-13 16:51 | Undetermined | Undetermined | 0 | WPT
| 448 | 2012-09-29 11:20 | Undetermined | Undetermined | 0 | WPT
| 448 | 2012-10-23 10:34 | Undetermined | Undetermined | 0 | WPT
| 448 | 2013-01-05 23:01 | Undetermined | Undetermined | 0 | WPT
| 448 | 2013-05-06 19:00 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2013-06-28 16:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT
| 448 | 2013-06-28 17:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT
| 448 | 2013-06-30 15:13 | Weather | Ice or snow/Equipment failure | 0 | WPT
| 448 | 2013-09-02 14:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT
| 448 | 2014-04-05 06:41 | Foreign Object | Bird contact | 0 | WPT
| 448 | 2014-04-29 08:44 | Weather | Tree fell on line due to storm/wind | 0 | WPT
| 448 | 2014-08-01 14:03 | Weather | Lightning Arrester/Transformer failure | 0 | WPT
| 448 | 2014-09-04 05:06 | Undetermined | Undetermined | 0 | WPT
| 448 | 2014-11-12 10:43 | Undetermined | Undetermined | 0 | WPT
| 448 | 2015-01-02 14:48 | Equipment | Fuse overloaded/inadequate fuse size | 0 | WPT
| 449 | 2005-07-05 05:39 | Undetermined | Undetermined | 1 | MOR
| 449 | 2005-07-18 16:42 | Undetermined | Undetermined | 0 | MOR
| 449 | 2005-07-18 18:28 | Undetermined | Undetermined | 0 | MOR
| 449 | 2005-08-01 13:07 | Weather | Lightning Arrester/Transformer failure | 0 | MOR
| 449 | 2006-05-19 12:40 | Customer Contact | Vehicle contact | 0 | MOR
| 449 | 2006-05-30 23:05 | Foreign Object | Animal contact | 0 | MOR
| 449 | 2006-07-15 15:04 | Weather | Lightning Arrester/Transformer failure | 1 | MOR
| 449 | 2006-10-14 02:08 | Weather | Lightning Arrester/Transformer failure | 0 | MOR
| 449 | 2006-11-15 12:46 | Undetermined | Undetermined | 0 | MOR
| 449 | 2007-08-15 16:18 | Undetermined | Undetermined | 0 | MOR
| 449 | 2008-08-21 20:33 | Undetermined | Undetermined | 0 | MOR
| 449 | 2008-09-03 16:36 | Equipment | Conductor failure/wire down | 0 | MOR
| 449 | 2008-10-14 04:52 | Undetermined | Undetermined | 0 | MOR
| 449 | 2009-02-10 06:59 | Undetermined | Undetermined | 0 | MOR
| 449 | 2009-08-22 07:31 | Equipment | Transformer faulted/mechanical | 0 | MOR
| 449 | 2009-11-07 02:57 | Undetermined | Undetermined | 0 | MOR
| 449 | 2009-11-30 09:06 | Equipment | Insulator/pin failure/wire floating | 0 | MOR
| 449 | 2009-12-07 14:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MOR
| 449 | 2009-12-13 06:48 | Undetermined | Undetermined | 0 | MOR
| 449 | 2009-12-22 09:04 | Weather | Ice or snow/Equipment failure | 0 | MOR
| 449 | 2010-01-19 16:16 | Equipment | Cutout failure | 0 | MOR
| 449 | 2011-02-02 09:01 | Equipment | Transformer faulted/mechanical | 0 | MOR
| 449 | 2011-08-27 10:13 | Undetermined | Undetermined | 0 | MOR
| 449 | 2011-08-28 14:52 | Weather | Lightning Arrester/Transformer failure | 0 | MOR
| 449 | 2011-10-12 16:22 | Undetermined | Undetermined | 0 | MOR
| 449 | 2012-07-30 14:47 | Weather | Lightning Arrester/Transformer failure | 0 | MOR
| 449 | 2012-08-13 06:53 | Foreign Object | Bird contact | 0 | MOR
| 449 | 2013-05-07 07:34 | Foreign Object | Bird contact | 0 | MOR
| 449 | 2013-05-25 16:18 | Undetermined | Undetermined | 0 | MOR
| 449 | 2013-07-01 07:54 | Undetermined | Undetermined | 0 | MOR
| 449 | 2013-09-08 07:00 | Weather | Flood | 0 | MOR
| 449 | 2014-04-30 10:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MOR
| 449 | 2014-07-21 15:41 | Foreign Object | Animal contact | 0 | MOR
| 449 | 2014-08-17 16:59 | Undetermined | Undetermined | 0 | MOR
| 449 | 2015-02-26 06:25 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MOR
| 450 | 2005-02-22 11:23 | Weather | Tree contact due to storm/high wind | 0 | ESC
| 450 | 2005-11-25 15:53 | Tree Contact | Tree fell on line | 0 | ESC
| 450 | 2006-01-02 20:33 | Weather | Tree fell on line due to storm/wind | 0 | ESC
| 450 | 2006-03-13 12:56 | Equipment | Transformer faulted/mechanical | 0 | ESC
| 450 | 2006-04-03 22:16 | Equipment | Transformer faulted/mechanical | 0 | ESC
| 450 | 2006-06-14 08:55 | Undetermined | Undetermined | 0 | ESC
| 450 | 2006-06-15 01:38 | Customer Contact | Vehicle contact | 0 | ESC
| 450 | 2007-02-08 11:44 | Undetermined | Undetermined | 0 | ESC
| 450 | 2007-06-13 15:30 | Tree Contact | Tree fell on line | 0 | ESC
| 450 | 2007-09-01 16:14 | Weather | Lightning Arrester/Transformer failure | 0 | ESC
| 450 | 2008-01-20 20:23 | Customer Contact | Vehicle contact | 0 | ESC
| 450 | 2008-04-15 20:18 | Undetermined | Undetermined | 0 | ESC
| 450 | 2008-07-13 20:05 | Undetermined | Undetermined | 1 | ESC
| 450 | 2009-06-15 13:13 | Customer Contact | Line fault/tree trimming | 0 | ESC
| 450 | 2009-07-05 08:51 | Foreign Object | Bird contact | 1 | ESC
| 450 | 2009-08-04 13:54 | Customer Contact | Vehicle contact | 0 | ESC
| 450 | 2010-01-21 12:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ESC
| 450 | 2010-12-23 13:22 | Equipment | Cutout failure | 0 | ESC
| 450 | 2011-08-28 15:55 | Undetermined | Undetermined | 0 | ESC
| 450 | 2011-12-13 02:32 | Undetermined | Undetermined | 0 | ESC
| 450 | 2012-01-16 06:40 | Weather | Tree fell on line due to storm/wind | 0 | ESC
| 450 | 2012-09-10 14:50 | Weather | Lightning Arrester/Transformer failure | 0 | ESC
| 450 | 2013-04-09 20:43 | Customer Contact | Vehicle contact | 0 | ESC
| 450 | 2013-05-10 13:25 | Undetermined | Undetermined | 0 | ESC
| 450 | 2013-11-02 01:58 | Tree Contact | Tree fell on line | 0 | ESC
| 450 | 2014-04-26 07:28 | Undetermined | Undetermined | 0 | ESC
| 450 | 2014-08-17 17:40 | Undetermined | Undetermined | 0 | ESC
| 450 | 2014-09-07 13:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ESC
| 456 | 2005-09-20 09:19 | Weather | Lightning Arrester/Transformer failure | 0 | ESC
| 456 | 2006-11-29 18:29 | Weather | Palm frond contact due to storm/wind | 0 | ESC
| 456 | 2007-08-26 06:23 | Weather | Lightning Arrester/Transformer failure | 0 | ESC
| 456 | 2007-08-26 07:52 | Weather | Lightning Arrester/Transformer failure | 0 | ESC
| 456 | 2008-07-27 14:23 | Equipment | Arrester (lightning) failure | 0 | ESC
| 456 | 2008-09-12 13:21 | Customer Contact | Line fault/tree trimming | 0 | ESC
| 456 | 2008-11-13 06:43 | Foreign Object | Bird contact | 0 | ESC
| 456 | 2010-04-16 19:35 | Equipment | Fuse holder/fuse cabinet failed | 0 | ESC
| 456 | 2013-05-19 03:29 | Customer Contact | Vehicle contact | 0 | ESC
| 456 | 2014-11-21 14:03 | Equipment | Transformer faulted/mechanical | 0 | ESC
| 470 | 2005-04-29 05:18 | Weather | Tree fell on line due to storm/wind | 0 | HVW
| 470 | 2005-08-05 08:14 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2005-09-09 12:24 | Foreign Object | Bird contact | 0 | HVW
| 470 | 2005-09-20 20:47 | Weather | Lightning Arrester/Transformer failure | 0 | HVW
| 470 | 2005-09-22 12:27 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2005-12-02 05:28 | Undetermined | Undetermined | 0 | HVW
| 470 | 2006-03-10 20:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2006-10-26 11:00 | Undetermined | Undetermined | 0 | HVW
| 470 | 2006-10-26 13:50 | Undetermined | Undetermined | 0 | HVW
| 470 | 2007-03-03 10:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2007-03-03 16:34 | Weather | Wind - wires slap/pole down | 0 | HVW
| 470 | 2007-03-16 17:52 | Undetermined | Undetermined | 0 | HVW
| 470 | 2007-04-23 02:55 | Weather | Tree fell on line due to storm/wind | 0 | HVW
| 470 | 2007-04-29 04:40 | Foreign Object | Vandalism | 0 | HVW
| 470 | 2007-08-26 09:13 | Weather | Lightning Arrester/Transformer failure | 0 | HVW
| 470 | 2007-09-28 10:10 | Foreign Object | Foreign object in distribution line | 0 | HVW
| 470 | 2007-11-16 11:59 | Undetermined | Undetermined | 0 | HVW
| 470 | 2008-09-21 08:24 | Foreign Object | Foreign object in distribution line | 0 | HVW
| 470 | 2008-12-06 09:40 | Customer Contact | Heavy equp contact/digin | 0 | HVW
| 470 | 2008-12-15 10:01 | Undetermined | Undetermined | 0 | HVW
| 470 | 2009-09-23 17:51 | Undetermined | Undetermined | 0 | HVW
| 470 | 2009-10-23 10:34 | Customer Contact | Heavy equp contact/digin | 0 | HVW
| 470 | 2009-12-01 05:10 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2010-01-13 14:44 | Foreign Object | Bird contact | 0 | HVW
| 470 | 2010-01-13 15:27 | Foreign Object | Bird contact | 0 | HVW
| 470 | 2010-01-18 13:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2010-01-21 07:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2010-02-27 10:08 | Undetermined | Undetermined | 0 | HVW
| 470 | 2010-09-17 20:37 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2011-02-18 22:36 | Undetermined | Undetermined | 0 | HVW
| 470 | 2011-03-20 15:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2011-03-20 17:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2011-03-20 18:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2011-04-11 08:58 | Foreign Object | Bird contact | 0 | HVW
| 470 | 2011-07-04 07:31 | Undetermined | Undetermined | 1 | HVW
| 470 | 2012-01-02 06:55 | Undetermined | Undetermined | 0 | HVW
| 470 | 2012-01-08 11:53 | Foreign Object | Bird contact | 0 | HVW
| 470 | 2012-03-26 14:57 | Foreign Object | Bird contact | 0 | HVW
| 470 | 2012-10-29 10:45 | Equipment | Transformer faulted/mechanical | 0 | HVW
| 470 | 2012-11-08 04:13 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2013-01-31 09:43 | Customer Contact | Heavy equp contact/digin | 0 | HVW
| 470 | 2013-08-17 07:43 | Equipment | Arrester (lightning) failure | 0 | HVW
| 470 | 2013-10-08 01:54 | Equipment | Crossarm failure | 0 | HVW
| 470 | 2013-10-26 07:48 | Equipment | Arrester (lightning) failure | 0 | HVW
| 470 | 2014-02-19 18:48 | Undetermined | Undetermined | 0 | HVW
| 470 | 2014-04-30 13:07 | Weather | Tree fell on line due to storm/wind | 0 | HVW
| 470 | 2014-05-13 12:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW
| 470 | 2014-05-14 09:47 | Undetermined | Undetermined | 0 | HVW
| 470 | 2014-06-19 16:43 | Customer Contact | Personnel contact | 0 | HVW
| 470 | 2014-10-22 06:16 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2014-11-01 04:02 | Equipment | Transformer faulted/mechanical | 0 | HVW
| 470 | 2014-11-17 21:24 | Customer Contact | Vehicle contact | 0 | HVW
| 470 | 2015-01-25 10:15 | Undetermined | Undetermined | 0 | HVW
| 48 | 2008-02-02 13:20 | Equipment | Insulator/pin failure/wire floating | 0 | KSAN
| 48 | 2008-07-11 06:43 | Equipment | Switch faulted/mechanical | 1 | KSAN
| 48 | 2014-09-10 06:55 | Equipment | Arrester (lightning) failure | 0 | KSAN
| 48 | 2014-12-02 23:20 | Customer Contact | Vehicle contact | 0 | KSAN
| 500 | 2013-05-02 16:06 | Equipment | Pole broke/rotted/on fire | 0 | MPE
| 520 | 2005-02-23 04:37 | Weather | Wind - wires slap/pole down | 0 | DLZ
| 520 | 2005-04-08 11:00 | Customer Contact | Line fault/tree trimming | 0 | DLZ
| 520 | 2005-05-07 22:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 520 | 2005-07-21 06:49 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2005-08-02 08:17 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2005-08-27 18:17 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2005-09-09 14:09 | Equipment | Transformer faulted/mechanical | 0 | DLZ
| 520 | 2005-09-20 06:27 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2005-09-20 18:45 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2006-01-15 14:18 | Weather | Tree fell on line due to storm/wind | 0 | DLZ
| 520 | 2006-02-15 14:55 | Equipment | Crossarm failure | 0 | DLZ
| 520 | 2006-04-06 19:51 | Equipment | Regulator faulted/mechanical | 0 | DLZ
| 520 | 2006-07-04 08:32 | Undetermined | Undetermined | 1 | DLZ
| 520 | 2006-07-04 13:47 | Equipment | Fuse overloaded/inadequate fuse size | 1 | DLZ
| 520 | 2006-07-15 08:07 | Equipment | Fuse holder/fuse cabinet failed | 1 | DLZ
| 520 | 2006-07-17 01:52 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2006-12-05 12:11 | Customer Contact | Heavy equp contact/digin | 0 | DLZ
| 520 | 2006-12-25 13:44 | Foreign Object | Damage by gunshot | 0 | DLZ
| 520 | 2007-01-05 11:42 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2007-03-29 06:45 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2007-06-07 05:38 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2007-07-09 08:20 | Foreign Object | Bird contact | 1 | DLZ
| 520 | 2007-07-24 19:04 | Equipment | Fuse holder/fuse cabinet failed | 0 | DLZ
| 520 | 2007-08-30 11:32 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2007-09-01 14:13 | Equipment | Fuse overloaded/inadequate fuse size | 0 | DLZ
| 520 | 2007-10-21 11:16 | Weather | Wind - wires slap/pole down | 0 | DLZ
| 520 | 2008-01-05 07:30 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2008-05-22 19:51 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2008-07-10 09:18 | Undetermined | Undetermined | 1 | DLZ
| 520 | 2008-10-14 08:58 | Weather | Tree fell on line due to storm/wind | 0 | DLZ
| 520 | 2008-10-20 07:24 | Foreign Object | Bird contact | 0 | DLZ
| 520 | 2009-06-25 08:01 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 520 | 2009-07-21 14:55 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2009-08-06 09:18 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2010-01-21 21:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2010-03-14 18:28 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2010-04-04 14:14 | Equipment | Fuse holder/fuse cabinet failed | 0 | DLZ
| 520 | 2010-04-30 21:06 | Foreign Object | Bird contact | 0 | DLZ
| 520 | 2010-05-25 07:56 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2010-06-11 03:20 | Foreign Object | Bird contact | 0 | DLZ
| 520 | 2010-06-17 16:34 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2010-06-27 18:19 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2010-09-30 10:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2010-09-30 14:55 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2010-10-19 09:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2010-10-19 09:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2010-10-19 13:38 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2010-10-19 15:35 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2010-10-19 16:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2010-10-19 16:39 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2010-10-25 08:17 | Equipment | Fuse holder/fuse cabinet failed | 0 | DLZ
| 520 | 2010-11-02 10:13 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2011-02-04 12:49 | Equipment | Crossarm failure | 0 | DLZ
| 520 | 2011-03-12 00:03 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2011-03-13 12:31 | Foreign Object | Bird contact | 0 | DLZ
| 520 | 2011-03-28 07:11 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2011-05-19 13:12 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2011-07-21 08:36 | Foreign Object | Animal contact | 0 | DLZ
| 520 | 2011-09-26 07:21 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2012-03-18 18:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2012-03-19 05:54 | Weather | Tree fell on line due to storm/wind | 0 | DLZ
| 520 | 2012-04-04 10:57 | Equipment | Conductor failure/wire down | 0 | DLZ
| 520 | 2012-04-22 05:07 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 520 | 2012-05-14 16:08 | Equipment | SCADA Malfunction | 0 | DLZ
| 520 | 2012-05-15 18:00 | Foreign Object | Damage by gunshot | 0 | DLZ
| 520 | 2012-05-23 10:27 | Equipment | Transformer faulted/mechanical | 0 | DLZ
| 520 | 2012-05-23 11:15 | Equipment | Transformer faulted/mechanical | 0 | DLZ
| 520 | 2012-06-09 07:41 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2012-08-25 20:05 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 520 | 2012-09-14 15:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ
| 520 | 2012-09-15 16:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 520 | 2012-12-20 05:18 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2013-04-02 10:07 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2013-04-25 08:16 | Equipment | SCADA Malfunction | 0 | DLZ
| 520 | 2013-05-02 17:29 | Equipment | Pole broke/rotted/on fire | 0 | DLZ
| 520 | 2013-06-11 05:35 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2013-06-16 09:10 | Foreign Object | Bird contact | 0 | DLZ
| 520 | 2013-08-02 11:57 | Equipment | Fuse overloaded/inadequate fuse size | 0 | DLZ
| 520 | 2013-09-05 22:34 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2013-10-14 03:56 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2014-01-06 10:35 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-02-13 18:22 | Tree Contact | Tree fell on line | 0 | DLZ
| 520 | 2014-03-02 07:18 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2014-03-05 14:10 | Equipment | Transformer faulted/mechanical | 0 | DLZ
| 520 | 2014-03-19 09:24 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-03-31 15:38 | Tree Contact | Tree fell on line | 0 | DLZ
| 520 | 2014-04-01 08:03 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-04-02 17:58 | Customer Contact | Vehicle contact | 0 | DLZ
| 520 | 2014-04-13 09:32 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-04-16 16:31 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-05-10 17:11 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-06-27 09:51 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 520 | 2014-07-22 09:25 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-08-20 03:14 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2014-08-20 03:14 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2014-08-20 05:31 | Undetermined | Undetermined | 0 | DLZ
| 520 | 2014-08-20 08:17 | Weather | Lightning Arrester/Transformer failure | 0 | DLZ
| 520 | 2015-01-05 15:25 | Tree Contact | Tree fell on line | 0 | DLZ
| 520 | 2015-03-02 12:32 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ
| 521 | 2005-01-07 16:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV
| 521 | 2005-02-03 10:13 | Weather | Tree fell on line due to storm/wind | 0 | RBV
| 521 | 2005-02-19 09:12 | Weather | Wind - wires slap/pole down | 0 | RBV
| 521 | 2005-02-24 19:15 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2005-02-24 23:33 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2005-06-18 17:49 | Undetermined | Undetermined | 0 | RBV
| 521 | 2005-08-24 10:06 | Equipment | Arrester (lightning) failure | 0 | RBV
| 521 | 2005-09-19 17:46 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2005-09-21 11:19 | Undetermined | Undetermined | 0 | RBV
| 521 | 2005-09-24 08:57 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2005-12-07 09:21 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2005-12-24 13:18 | Undetermined | Undetermined | 0 | RBV
| 521 | 2006-03-20 10:51 | Equipment | Cutout failure | 0 | RBV
| 521 | 2006-05-06 18:44 | Undetermined | Undetermined | 0 | RBV
| 521 | 2006-09-29 10:22 | Undetermined | Undetermined | 0 | RBV
| 521 | 2006-12-21 13:21 | Equipment | Fuse overloaded/inadequate fuse size | 0 | RBV
| 521 | 2007-03-05 07:28 | Undetermined | Undetermined | 0 | RBV
| 521 | 2007-04-12 14:50 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2007-05-11 10:36 | Equipment | Transformer faulted/mechanical | 0 | RBV
| 521 | 2007-06-17 11:07 | Undetermined | Undetermined | 0 | RBV
| 521 | 2007-07-16 13:41 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2007-09-21 03:41 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2008-01-14 13:01 | Foreign Object | Animal contact | 0 | RBV
| 521 | 2008-02-03 19:34 | Weather | Wind - wires slap/pole down | 0 | RBV
| 521 | 2008-05-05 21:33 | Equipment | Fuse holder/fuse cabinet failed | 0 | RBV
| 521 | 2008-05-31 07:29 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2008-06-07 13:26 | Undetermined | Undetermined | 0 | RBV
| 521 | 2008-07-25 19:57 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2008-08-22 09:28 | Undetermined | Undetermined | 0 | RBV
| 521 | 2008-11-03 08:27 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2008-11-04 17:27 | Equipment | Cutout failure | 0 | RBV
| 521 | 2008-11-23 23:00 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2008-11-27 04:44 | Tree Contact | Tree fell on line | 0 | RBV
| 521 | 2009-01-24 08:25 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2009-01-27 20:24 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBV
| 521 | 2009-05-22 17:54 | Foreign Object | Foreign object in distribution line | 0 | RBV
| 521 | 2009-06-03 12:27 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2009-06-03 19:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV
| 521 | 2009-06-03 19:59 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2009-09-06 04:25 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2009-10-13 07:35 | Undetermined | Undetermined | 0 | RBV
| 521 | 2009-10-23 12:58 | Undetermined | Undetermined | 0 | RBV
| 521 | 2009-11-28 17:23 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2009-12-29 15:18 | Undetermined | Undetermined | 0 | RBV
| 521 | 2010-01-29 16:11 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2010-04-28 18:10 | Weather | Wind - wires slap/pole down | 0 | RBV
| 521 | 2010-07-30 08:27 | Foreign Object | Damage by gunshot | 0 | RBV
| 521 | 2010-08-02 14:34 | Equipment | Transformer faulted/mechanical | 0 | RBV
| 521 | 2010-09-06 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2010-09-30 18:38 | Weather | Ice or snow/Equipment failure | 0 | RBV
| 521 | 2010-10-19 16:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV
| 521 | 2010-12-04 21:07 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2011-01-02 17:41 | Equipment | Fuse holder/fuse cabinet failed | 0 | RBV
| 521 | 2011-03-16 11:48 | Undetermined | Undetermined | 0 | RBV
| 521 | 2011-03-17 14:08 | Equipment | Conductor failure/wire down | 0 | RBV
| 521 | 2011-05-04 09:45 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2011-05-06 13:19 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2011-05-12 23:08 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2011-09-19 11:19 | Undetermined | Undetermined | 0 | RBV
| 521 | 2011-11-20 11:47 | Undetermined | Undetermined | 0 | RBV
| 521 | 2012-01-07 03:35 | Equipment | Insulator/pin failure/wire floating | 0 | RBV
| 521 | 2012-05-28 06:29 | Tree Contact | Tree fell on line | 0 | RBV
| 521 | 2012-06-16 12:28 | Undetermined | Undetermined | 0 | RBV
| 521 | 2012-08-15 10:57 | Undetermined | Undetermined | 0 | RBV
| 521 | 2012-10-12 00:18 | Undetermined | Undetermined | 0 | RBV
| 521 | 2012-11-21 04:43 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2013-01-07 21:58 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2013-03-06 07:02 | Equipment | Recloser/breaker faulted/mechanical | 0 | RBV
| 521 | 2013-06-04 22:34 | Undetermined | Undetermined | 0 | RBV
| 521 | 2014-04-13 17:13 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2014-07-24 17:14 | Undetermined | Undetermined | 0 | RBV
| 521 | 2014-08-20 07:43 | Weather | Lightning Arrester/Transformer failure | 0 | RBV
| 521 | 2014-08-31 18:30 | Customer Contact | Vehicle contact | 0 | RBV
| 521 | 2014-09-14 14:54 | Undetermined | Undetermined | 0 | RBV
| 521 | 2014-09-16 16:13 | Equipment | Pole broke/rotted/on fire | 0 | RBV
| 521 | 2014-12-03 09:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV
| 521 | 2014-12-03 11:26 | Equipment | Transformer faulted/mechanical | 0 | RBV
| 521 | 2015-01-12 16:26 | Equipment | Arrester (lightning) failure | 0 | RBV
| 521 | 2015-01-31 12:18 | Foreign Object | Bird contact | 0 | RBV
| 521 | 2015-02-09 21:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBV
| 521 | 2015-03-15 07:42 | Undetermined | Undetermined | 0 | RBV
| 521 | 2015-03-17 23:34 | Equipment | Fuse holder/fuse cabinet failed | 0 | RBV
| 524 | 2005-02-11 09:48 | Weather | Wind - wires slap/pole down | 0 | LSV
| 524 | 2005-02-25 17:44 | Undetermined | Undetermined | 0 | LSV
| 524 | 2005-03-02 12:07 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2005-08-02 20:44 | Undetermined | Undetermined | 0 | LSV
| 524 | 2005-10-22 08:46 | Foreign Object | Animal contact | 0 | LSV
| 524 | 2006-01-25 07:04 | Weather | Wind - wires slap/pole down | 0 | LSV
| 524 | 2006-02-10 16:58 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2006-02-21 01:47 | Undetermined | Undetermined | 0 | LSV
| 524 | 2006-06-02 05:30 | Undetermined | Undetermined | 0 | LSV
| 524 | 2006-10-13 20:19 | Weather | Lightning Arrester/Transformer failure | 0 | LSV
| 524 | 2007-01-28 07:09 | Equipment | Transformer faulted/mechanical | 0 | LSV
| 524 | 2007-03-09 18:12 | Equipment | Crossarm failure | 0 | LSV
| 524 | 2007-03-22 17:28 | Weather | Lightning Arrester/Transformer failure | 0 | LSV
| 524 | 2007-04-01 07:09 | Equipment | Crossarm failure | 0 | LSV
| 524 | 2007-10-21 19:40 | Weather | Wind - wires slap/pole down | 0 | LSV
| 524 | 2007-10-22 06:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2007-10-22 12:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2007-10-29 17:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2007-11-30 09:21 | Equipment | Transformer faulted/mechanical | 0 | LSV
| 524 | 2007-12-01 01:24 | Equipment | Conductor failure/wire down | 0 | LSV
| 524 | 2008-01-03 08:19 | Undetermined | Undetermined | 0 | LSV
| 524 | 2008-01-15 14:37 | Foreign Object | Bird contact | 0 | LSV
| 524 | 2008-05-30 03:16 | Undetermined | Undetermined | 0 | LSV
| 524 | 2008-06-18 04:30 | Undetermined | Undetermined | 0 | LSV
| 524 | 2008-07-14 16:08 | Undetermined | Undetermined | 1 | LSV
| 524 | 2008-11-14 16:00 | Equipment | Pole broke/rotted/on fire | 0 | LSV
| 524 | 2008-12-18 04:19 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2009-01-14 07:17 | Undetermined | Undetermined | 0 | LSV
| 524 | 2009-02-15 08:26 | Undetermined | Undetermined | 0 | LSV
| 524 | 2009-05-29 07:08 | Undetermined | Undetermined | 0 | LSV
| 524 | 2009-08-28 14:40 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2009-12-07 14:37 | Weather | Wind - wires slap/pole down | 0 | LSV
| 524 | 2010-01-18 23:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2010-01-19 14:33 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2010-01-19 18:53 | Weather | Wind - wires slap/pole down | 0 | LSV
| 524 | 2010-01-21 06:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2010-01-22 01:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2010-02-01 21:30 | Equipment | Pole broke/rotted/on fire | 0 | LSV
| 524 | 2010-02-08 07:52 | Undetermined | Undetermined | 0 | LSV
| 524 | 2010-05-30 19:39 | Equipment | Transformer faulted/mechanical | 0 | LSV
| 524 | 2010-06-08 15:36 | Equipment | Transformer faulted/mechanical | 0 | LSV
| 524 | 2010-09-05 20:41 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2010-09-22 09:38 | Equipment | Transformer faulted/mechanical | 0 | LSV
| 524 | 2010-09-30 13:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2010-10-06 18:50 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LSV
| 524 | 2010-10-19 21:35 | Weather | Wind - wires slap/pole down | 0 | LSV
| 524 | 2011-04-01 13:49 | Equipment | Crossarm failure | 0 | LSV
| 524 | 2011-06-18 17:44 | Undetermined | Undetermined | 0 | LSV
| 524 | 2011-10-12 12:55 | Equipment | Conductor failure/wire down | 0 | LSV
| 524 | 2011-11-21 04:29 | Equipment | Arrester (lightning) failure | 0 | LSV
| 524 | 2012-01-21 07:24 | Foreign Object | Bird contact | 0 | LSV
| 524 | 2012-02-01 16:52 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2012-02-02 01:47 | Customer Contact | Vehicle contact | 0 | LSV
| 524 | 2012-02-06 10:31 | Equipment | Cutout failure | 0 | LSV
| 524 | 2012-02-22 13:44 | Customer Contact | Line fault/tree trimming | 0 | LSV
| 524 | 2012-03-26 18:42 | Foreign Object | Bird contact | 0 | LSV
| 524 | 2012-04-10 07:37 | Undetermined | Undetermined | 0 | LSV
| 524 | 2012-07-10 09:15 | Customer Contact | Vehicle contact | 1 | LSV
| 524 | 2012-07-21 10:22 | Foreign Object | Bird contact | 0 | LSV
| 524 | 2012-07-30 19:20 | Undetermined | Undetermined | 0 | LSV
| 524 | 2013-04-28 13:24 | Foreign Object | Foreign object in distribution line | 0 | LSV
| 524 | 2013-09-14 18:37 | Undetermined | Undetermined | 0 | LSV
| 524 | 2013-10-10 12:47 | Customer Contact | Line fault/tree trimming | 0 | LSV
| 524 | 2013-10-30 06:42 | Undetermined | Undetermined | 0 | LSV
| 524 | 2014-07-26 13:40 | Equipment | Pole broke/rotted/on fire | 0 | LSV
| 524 | 2014-07-31 14:59 | Undetermined | Undetermined | 0 | LSV
| 524 | 2014-09-17 21:47 | Undetermined | Undetermined | 0 | LSV
| 524 | 2014-12-03 02:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV
| 524 | 2015-01-26 13:12 | Equipment | Transformer faulted/mechanical | 0 | LSV
| 524 | 2015-02-19 10:18 | Undetermined | Undetermined | 0 | LSV
| 524 | 2015-03-14 02:02 | Customer Contact | Vehicle contact | 0 | LSV
| 67 | 2005-07-06 04:52 | Undetermined | Undetermined | 1 | DHV
| 67 | 2005-07-23 00:55 | Weather | Lightning Arrester/Transformer failure | 0 | DHV
| 67 | 2006-01-02 06:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DHV
| 67 | 2006-04-26 02:59 | Undetermined | Undetermined | 0 | DHV
| 67 | 2006-12-24 08:24 | Undetermined | Undetermined | 0 | DHV
| 67 | 2007-01-12 00:10 | Equipment | Insulator/pin failure/wire floating | 0 | DHV
| 67 | 2007-03-20 08:30 | Customer Contact | Vehicle contact | 0 | DHV
| 67 | 2007-08-30 15:47 | Weather | Lightning Arrester/Transformer failure | 0 | DHV
| 67 | 2007-09-03 22:36 | Undetermined | Undetermined | 0 | DHV
| 67 | 2008-10-05 09:35 | Equipment | Arrester (lightning) failure | 0 | DHV
| 67 | 2008-12-15 14:40 | Undetermined | Undetermined | 0 | DHV
| 67 | 2009-03-29 10:20 | Foreign Object | Bird contact | 0 | DHV
| 67 | 2009-07-18 18:35 | Customer Contact | Vehicle contact | 0 | DHV
| 67 | 2009-11-14 06:53 | Foreign Object | Bird contact | 0 | DHV
| 67 | 2009-12-07 17:14 | Weather | Wind - wires slap/pole down | 0 | DHV
| 67 | 2010-01-19 14:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DHV
| 67 | 2010-05-07 07:49 | Equipment | Transformer faulted/mechanical | 0 | DHV
| 67 | 2010-10-22 20:44 | Undetermined | Undetermined | 0 | DHV
| 67 | 2011-03-09 14:28 | Customer Contact | Vehicle contact | 0 | DHV
| 67 | 2011-04-12 08:26 | Undetermined | Undetermined | 0 | DHV
| 67 | 2012-02-05 09:48 | Foreign Object | Bird contact | 0 | DHV
| 67 | 2012-05-23 10:46 | Equipment | Transformer faulted/mechanical | 0 | DHV
| 67 | 2012-09-10 14:46 | Weather | Lightning Arrester/Transformer failure | 0 | DHV
| 67 | 2012-09-10 14:53 | Weather | Lightning Arrester/Transformer failure | 0 | DHV
| 67 | 2012-09-10 16:27 | Weather | Lightning Arrester/Transformer failure | 0 | DHV
| 67 | 2012-10-15 07:41 | Foreign Object | Bird contact | 0 | DHV
| 67 | 2012-10-20 08:28 | Undetermined | Undetermined | 0 | DHV
| 67 | 2012-11-17 08:31 | Equipment | Transformer faulted/mechanical | 0 | DHV
| 67 | 2013-03-04 22:53 | Undetermined | Undetermined | 0 | DHV
| 67 | 2013-03-07 23:03 | Equipment | Transformer faulted/mechanical | 0 | DHV
| 67 | 2013-04-20 07:57 | Undetermined | Undetermined | 0 | DHV
| 67 | 2013-06-17 05:17 | Undetermined | Undetermined | 0 | DHV
| 67 | 2013-07-25 20:53 | Equipment | Transformer faulted/mechanical | 0 | DHV
| 67 | 2013-12-04 01:40 | Undetermined | Undetermined | 0 | DHV
| 67 | 2013-12-30 12:43 | Customer Contact | Heavy equp contact/digin | 0 | DHV
| 67 | 2014-02-28 08:03 | Foreign Object | Foreign object in distribution line | 0 | DHV
| 67 | 2014-08-03 12:02 | Undetermined | Undetermined | 0 | DHV
| 67 | 2014-08-03 21:00 | Weather | Lightning Arrester/Transformer failure | 0 | DHV
| 67 | 2014-09-12 15:20 | Undetermined | Undetermined | 0 | DHV
| 67 | 2014-10-01 17:01 | Foreign Object | Bird contact | 0 | DHV
| 67 | 2014-10-28 10:50 | Undetermined | Undetermined | 0 | DHV
| 67 | 2014-11-02 02:29 | Undetermined | Undetermined | 0 | DHV
| 701 | 2005-04-29 08:17 | Undetermined | Undetermined | 0 | MVN
| 701 | 2005-09-20 02:09 | Weather | Lightning Arrester/Transformer failure | 0 | MVN
| 701 | 2005-09-20 02:10 | Weather | Lightning Arrester/Transformer failure | 0 | MVN
| 701 | 2006-06-27 08:42 | Weather | Lightning Arrester/Transformer failure | 0 | MVN
| 701 | 2007-06-20 10:54 | Foreign Object | Foreign object in distribution line | 0 | MVN
| 701 | 2007-10-07 09:42 | Undetermined | Undetermined | 0 | MVN
| 701 | 2007-10-29 10:34 | Foreign Object | Bird contact | 0 | MVN
| 701 | 2007-12-07 05:51 | Weather | Palm frond contact due to storm/wind | 0 | MVN
| 701 | 2009-11-07 13:01 | Foreign Object | Foreign object in distribution line | 0 | MVN
| 701 | 2013-12-16 14:24 | Undetermined | Undetermined | 0 | MVN
| 701 | 2014-09-16 17:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MVN
| 701 | 2015-01-20 11:21 | Customer Contact | Line fault/tree trimming | 0 | MVN
| 728 | 2005-01-27 11:45 | Undetermined | Undetermined | 0 | DMH
| 728 | 2005-02-05 00:40 | Undetermined | Undetermined | 0 | DMH
| 728 | 2009-09-29 22:48 | Equipment | Conductor failure/wire down | 0 | DMH
| 728 | 2013-08-31 01:28 | Weather | Ice or snow/Equipment failure | 0 | DMH
| 73 | 2005-05-05 10:32 | Undetermined | Undetermined | 0 | DEN
| 73 | 2005-06-21 19:52 | Tree Contact | Tree fell on line | 0 | DEN
| 73 | 2005-06-22 00:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DEN
| 73 | 2005-07-13 07:06 | Equipment | Crossarm failure | 1 | DEN
| 73 | 2005-07-23 13:31 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 73 | 2005-10-16 17:25 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 73 | 2005-10-26 19:15 | Foreign Object | Aircraft | 0 | DEN
| 73 | 2005-12-06 14:40 | Equipment | Transformer faulted/mechanical | 0 | DEN
| 73 | 2006-09-20 12:49 | Customer Contact | Heavy equp contact/digin | 0 | DEN
| 73 | 2007-01-01 11:21 | Undetermined | Undetermined | 0 | DEN
| 73 | 2007-04-29 06:00 | Undetermined | Undetermined | 0 | DEN
| 73 | 2007-06-11 17:28 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2007-06-23 10:56 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2007-10-22 04:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 73 | 2008-02-19 07:09 | Undetermined | Undetermined | 0 | DEN
| 73 | 2008-04-24 07:17 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2008-06-25 10:40 | Undetermined | Undetermined | 0 | DEN
| 73 | 2008-10-11 05:28 | Equipment | Cutout failure | 0 | DEN
| 73 | 2009-06-02 16:05 | Customer Contact | Vehicle contact | 0 | DEN
| 73 | 2009-09-08 22:09 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2009-12-07 17:21 | Weather | Wind - wires slap/pole down | 0 | DEN
| 73 | 2010-07-15 13:52 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 73 | 2010-07-15 14:17 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 73 | 2010-07-15 16:57 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 73 | 2010-09-30 10:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 73 | 2010-10-19 13:02 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 73 | 2011-07-05 18:42 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 73 | 2011-11-02 08:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 73 | 2012-08-11 15:42 | Undetermined | Undetermined | 0 | DEN
| 73 | 2012-09-06 16:40 | Undetermined | Undetermined | 0 | DEN
| 73 | 2012-09-29 10:49 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2012-10-23 08:28 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2013-09-01 14:11 | Foreign Object | Foreign object in distribution line | 0 | DEN
| 73 | 2013-09-04 16:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 73 | 2013-09-04 17:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 73 | 2013-10-01 03:26 | Foreign Object | Animal contact | 0 | DEN
| 73 | 2013-11-03 16:53 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2013-11-16 12:01 | Undetermined | Undetermined | 0 | DEN
| 73 | 2014-03-02 23:12 | Undetermined | Undetermined | 0 | DEN
| 73 | 2014-04-20 08:10 | Foreign Object | Bird contact | 0 | DEN
| 73 | 2014-04-30 06:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 73 | 2014-06-26 13:11 | Equipment | Arrester (lightning) failure | 0 | DEN
| 73 | 2014-08-03 20:51 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 73 | 2014-09-07 13:33 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 73 | 2014-12-03 08:33 | Undetermined | Undetermined | 0 | DEN
| 75 | 2005-01-04 10:13 | Equipment | Conductor failure/wire down | 0 | OTY
| 75 | 2005-01-11 09:19 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2005-01-16 15:47 | Equipment | Conductor failure/wire down | 0 | OTY
| 75 | 2005-01-17 11:03 | Undetermined | Undetermined | 0 | OTY
| 75 | 2005-02-11 01:54 | Equipment | Guy wire failure | 0 | OTY
| 75 | 2005-03-21 22:41 | Equipment | Regulator faulted/mechanical | 0 | OTY
| 75 | 2005-04-21 18:36 | Undetermined | Undetermined | 0 | OTY
| 75 | 2005-04-25 05:04 | Equipment | Arrester (lightning) failure | 0 | OTY
| 75 | 2005-06-09 09:11 | Customer Contact | Heavy equp contact/digin | 0 | OTY
| 75 | 2005-06-09 20:00 | Equipment | Arrester (lightning) failure | 0 | OTY
| 75 | 2005-09-20 15:53 | Weather | Lightning Arrester/Transformer failure | 0 | OTY
| 75 | 2005-10-29 13:25 | Equipment | Connector/jumper/splice/elbow/rack | 0 | OTY
| 75 | 2006-01-02 14:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2006-01-07 07:07 | Equipment | Conductor failure/wire down | 0 | OTY
| 75 | 2006-02-28 02:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2006-06-10 00:51 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2006-09-03 12:46 | Equipment | Recloser/breaker overloaded/electrical | 0 | OTY
| 75 | 2006-11-30 00:45 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2007-01-02 15:54 | Foreign Object | Foreign object in distribution line | 0 | OTY
| 75 | 2007-02-28 08:05 | Equipment | Arrester (lightning) failure | 0 | OTY
| 75 | 2007-03-03 07:53 | Weather | Tree fell on line due to storm/wind | 0 | OTY
| 75 | 2007-03-03 10:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2007-03-20 13:48 | Equipment | Regulator faulted/mechanical | 0 | OTY
| 75 | 2007-05-26 15:59 | Foreign Object | Foreign object in distribution line | 0 | OTY
| 75 | 2007-09-22 14:33 | Equipment | Connector/jumper/splice/elbow/rack | 0 | OTY
| 75 | 2007-10-09 11:35 | Undetermined | Undetermined | 0 | OTY
| 75 | 2007-10-22 07:11 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2007-10-25 15:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2007-10-26 17:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2007-11-19 10:58 | Undetermined | Undetermined | 0 | OTY
| 75 | 2007-11-30 09:24 | Undetermined | Undetermined | 0 | OTY
| 75 | 2007-12-23 17:20 | Undetermined | Undetermined | 0 | OTY
| 75 | 2008-01-07 00:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2008-01-07 00:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2008-01-07 07:25 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2008-04-18 17:57 | Customer Contact | Line fault/tree trimming | 0 | OTY
| 75 | 2008-06-19 13:21 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2008-06-26 22:47 | Equipment | Conductor failure/wire down | 0 | OTY
| 75 | 2008-06-27 08:54 | Undetermined | Undetermined | 0 | OTY
| 75 | 2008-10-30 09:27 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2008-11-09 12:17 | Undetermined | Undetermined | 0 | OTY
| 75 | 2008-11-16 13:02 | Undetermined | Undetermined | 0 | OTY
| 75 | 2008-12-09 12:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2008-12-09 12:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2008-12-09 14:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2009-01-29 15:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2009-02-09 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2009-02-24 08:05 | Equipment | Connector/jumper/splice/elbow/rack | 0 | OTY
| 75 | 2009-04-03 10:08 | Undetermined | Undetermined | 0 | OTY
| 75 | 2009-04-05 09:30 | Undetermined | Undetermined | 0 | OTY
| 75 | 2009-10-06 12:27 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2009-10-13 06:27 | Equipment | Arrester (lightning) failure | 0 | OTY
| 75 | 2009-11-22 07:09 | Equipment | Conductor failure/wire down | 0 | OTY
| 75 | 2009-12-07 16:30 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2009-12-09 14:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2010-01-19 14:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2010-01-20 04:15 | Equipment | Transformer faulted/mechanical | 0 | OTY
| 75 | 2010-01-20 10:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2010-01-20 11:10 | Equipment | Insulator/pin failure/wire floating | 0 | OTY
| 75 | 2010-01-21 20:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2010-01-22 08:02 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2010-01-22 10:58 | Weather | Lightning Arrester/Transformer failure | 0 | OTY
| 75 | 2010-06-22 00:48 | Equipment | Transformer faulted/mechanical | 0 | OTY
| 75 | 2010-07-14 17:25 | Equipment | Conductor contact/wire slap | 1 | OTY
| 75 | 2010-09-02 15:48 | Customer Contact | Line fault/tree trimming | 0 | OTY
| 75 | 2010-09-03 21:21 | Undetermined | Undetermined | 0 | OTY
| 75 | 2010-09-13 00:20 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2010-09-30 12:37 | Weather | Lightning Arrester/Transformer failure | 0 | OTY
| 75 | 2010-09-30 19:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2010-10-01 17:45 | Weather | Lightning Arrester/Transformer failure | 0 | OTY
| 75 | 2010-10-17 00:57 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2010-10-19 15:45 | Weather | Lightning Arrester/Transformer failure | 0 | OTY
| 75 | 2010-11-05 16:51 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2010-11-09 16:35 | Foreign Object | Damage by gunshot | 0 | OTY
| 75 | 2011-01-13 06:57 | Foreign Object | Animal contact | 0 | OTY
| 75 | 2011-02-02 14:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2011-02-05 15:01 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2011-04-17 12:56 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2011-04-21 19:16 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2011-06-28 19:01 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2011-08-26 14:52 | Undetermined | Undetermined | 0 | OTY
| 75 | 2011-09-06 18:29 | Weather | Lightning Arrester/Transformer failure | 0 | OTY
| 75 | 2011-10-05 22:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2011-12-06 08:41 | Undetermined | Undetermined | 0 | OTY
| 75 | 2012-02-12 09:54 | Foreign Object | Foreign object in distribution line | 0 | OTY
| 75 | 2012-02-13 16:59 | Equipment | Transformer faulted/mechanical | 0 | OTY
| 75 | 2012-03-17 11:45 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2012-03-23 07:33 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2012-03-26 14:22 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2012-03-29 20:33 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2012-04-09 16:28 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2012-05-25 11:52 | Equipment | Crossarm failure | 0 | OTY
| 75 | 2012-09-02 17:06 | Equipment | Regulator faulted/mechanical | 0 | OTY
| 75 | 2012-10-12 10:24 | Foreign Object | Foreign object in distribution line | 0 | OTY
| 75 | 2013-01-01 01:41 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2013-01-26 05:08 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2013-05-12 18:31 | Foreign Object | Bird contact | 0 | OTY
| 75 | 2013-07-26 18:50 | Undetermined | Undetermined | 0 | OTY
| 75 | 2013-09-04 02:48 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2014-03-01 05:41 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2014-03-06 13:00 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2014-05-01 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 75 | 2014-05-13 08:37 | Weather | Wind - wires slap/pole down | 0 | OTY
| 75 | 2014-05-14 08:56 | Undetermined | Undetermined | 0 | OTY
| 75 | 2014-07-31 17:41 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2014-08-06 11:30 | Customer Contact | Vehicle contact | 0 | OTY
| 75 | 2014-08-30 16:17 | Undetermined | Undetermined | 0 | OTY
| 75 | 2014-09-17 23:59 | Equipment | Regulator faulted/mechanical | 0 | OTY
| 78 | 2006-11-30 07:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VJS
| 78 | 2007-08-18 13:48 | Equipment | Arrester (lightning) failure | 0 | VJS
| 78 | 2007-11-02 18:33 | Undetermined | Undetermined | 0 | VJS
| 78 | 2008-11-26 04:13 | Equipment | Transformer faulted/mechanical | 0 | VJS
| 78 | 2009-09-02 11:48 | Undetermined | Undetermined | 0 | VJS
| 78 | 2010-04-02 08:55 | Foreign Object | Bird contact | 0 | VJS
| 78 | 2011-08-07 09:04 | Customer Contact | Vehicle contact | 0 | VJS
| 78 | 2012-01-24 01:29 | Equipment | Transformer faulted/mechanical | 0 | VJS
| 78 | 2012-03-18 09:46 | Weather | Wind - wires slap/pole down | 0 | VJS
| 78 | 2012-08-11 14:37 | Weather | Lightning Arrester/Transformer failure | 0 | VJS
| 78 | 2013-03-26 00:11 | Undetermined | Undetermined | 0 | VJS
| 78 | 2013-09-04 12:06 | Weather | Lightning Arrester/Transformer failure | 0 | VJS
| 78 | 2014-04-30 06:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VJS
| 78 | 2014-09-24 07:32 | Equipment | Transformer faulted/mechanical | 0 | VJS
| 79 | 2005-01-03 16:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2005-03-19 01:39 | Equipment | Pole broke/rotted/on fire | 0 | DEN
| 79 | 2005-03-19 08:03 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2005-03-31 10:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2005-03-31 15:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2005-04-17 23:28 | Foreign Object | Bird contact | 0 | DEN
| 79 | 2005-04-22 17:08 | Undetermined | Undetermined | 0 | DEN
| 79 | 2005-04-24 07:42 | Undetermined | Undetermined | 0 | DEN
| 79 | 2005-06-02 04:10 | Equipment | Crossarm failure | 0 | DEN
| 79 | 2005-06-02 23:41 | Equipment | Crossarm failure | 0 | DEN
| 79 | 2005-06-04 04:57 | Equipment | Crossarm failure | 0 | DEN
| 79 | 2005-06-06 06:31 | Equipment | Crossarm failure | 0 | DEN
| 79 | 2005-06-06 12:02 | Equipment | Crossarm failure | 0 | DEN
| 79 | 2005-07-29 17:41 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2005-09-19 08:05 | Undetermined | Undetermined | 0 | DEN
| 79 | 2005-09-27 20:50 | Undetermined | Undetermined | 0 | DEN
| 79 | 2005-12-23 14:25 | Foreign Object | Foreign object in distribution line | 0 | DEN
| 79 | 2006-03-12 02:46 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2006-03-12 15:22 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2006-04-24 16:54 | Undetermined | Undetermined | 0 | DEN
| 79 | 2006-04-29 19:33 | Undetermined | Undetermined | 0 | DEN
| 79 | 2006-06-24 06:15 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2006-07-15 15:39 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 79 | 2006-07-15 18:03 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 79 | 2006-11-29 22:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2007-01-29 06:24 | Undetermined | Undetermined | 0 | DEN
| 79 | 2007-03-28 10:40 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2007-04-10 07:12 | Weather | Tree fell on line due to storm/wind | 0 | DEN
| 79 | 2007-06-19 06:23 | Undetermined | Undetermined | 0 | DEN
| 79 | 2007-08-26 10:37 | Equipment | Hardware failure | 0 | DEN
| 79 | 2007-09-01 17:04 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2007-10-21 22:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2007-10-23 13:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2007-10-23 19:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2008-01-07 05:32 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2008-02-17 17:54 | Customer Contact | Vehicle contact | 0 | DEN
| 79 | 2008-03-02 00:50 | Equipment | Crossarm failure | 0 | DEN
| 79 | 2008-03-03 03:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2008-03-03 06:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2008-03-18 15:22 | Equipment | Conductor failure/wire down | 0 | DEN
| 79 | 2008-05-06 04:25 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2008-05-06 10:44 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2008-07-10 08:31 | Undetermined | Undetermined | 1 | DEN
| 79 | 2008-10-13 23:55 | Weather | Tree fell on line due to storm/wind | 0 | DEN
| 79 | 2008-12-18 03:41 | Weather | Tree fell on line due to storm/wind | 0 | DEN
| 79 | 2009-01-10 05:19 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2009-01-10 21:56 | Equipment | Insulator/pin failure/wire floating | 0 | DEN
| 79 | 2009-01-11 00:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2009-01-11 01:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2009-01-11 11:18 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2009-02-10 12:44 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2009-02-11 06:55 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DEN
| 79 | 2009-02-12 00:52 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2009-09-02 15:29 | Undetermined | Undetermined | 0 | DEN
| 79 | 2009-09-16 16:27 | Equipment | Arrester (lightning) failure | 0 | DEN
| 79 | 2009-11-28 12:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2009-12-07 21:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2009-12-08 10:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2010-01-23 11:09 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2010-03-04 11:02 | Equipment | Arrester (lightning) failure | 0 | DEN
| 79 | 2010-03-16 18:21 | Undetermined | Undetermined | 0 | DEN
| 79 | 2010-04-23 10:41 | Equipment | Conductor failure/wire down | 0 | DEN
| 79 | 2010-07-15 13:54 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 79 | 2010-07-15 16:58 | Weather | Lightning Arrester/Transformer failure | 1 | DEN
| 79 | 2010-07-24 19:45 | Foreign Object | Bird contact | 0 | DEN
| 79 | 2010-08-15 23:53 | Undetermined | Undetermined | 0 | DEN
| 79 | 2010-08-30 12:23 | Undetermined | Undetermined | 0 | DEN
| 79 | 2010-09-30 10:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2010-11-08 01:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DEN
| 79 | 2010-11-13 03:47 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2010-11-28 12:23 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-01-14 20:25 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-01-23 08:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2011-01-26 09:43 | Foreign Object | Foreign object in distribution line | 0 | DEN
| 79 | 2011-02-03 13:31 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-02-26 13:55 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2011-02-27 02:35 | Weather | Tree fell on line due to storm/wind | 0 | DEN
| 79 | 2011-02-27 15:22 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2011-03-04 07:02 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2011-03-07 10:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2011-03-07 12:41 | Equipment | Arrester (lightning) failure | 0 | DEN
| 79 | 2011-03-07 18:07 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-03-07 21:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2011-03-08 12:55 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2011-03-25 03:38 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2011-04-09 14:12 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2011-05-18 06:35 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-07-06 13:04 | Equipment | Crossarm failure | 1 | DEN
| 79 | 2011-07-11 17:15 | Equipment | Crossarm failure | 1 | DEN
| 79 | 2011-07-24 19:14 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-09-13 08:19 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2011-09-13 23:26 | Undetermined | Undetermined | 0 | DEN
| 79 | 2011-09-23 10:33 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2012-01-21 07:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2012-01-23 11:05 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-02-27 23:54 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2012-02-28 18:52 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-03-19 02:16 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2012-03-19 15:08 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2012-03-21 15:22 | Equipment | Pole broke/rotted/on fire | 0 | DEN
| 79 | 2012-03-22 12:39 | Equipment | Insulator/pin failure/wire floating | 0 | DEN
| 79 | 2012-03-25 17:45 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2012-03-26 05:23 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-04-01 14:00 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-04-14 07:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2012-04-15 11:27 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2012-06-09 15:14 | Foreign Object | Bird contact | 0 | DEN
| 79 | 2012-07-05 07:02 | Foreign Object | Bird contact | 1 | DEN
| 79 | 2012-07-17 08:57 | Equipment | Transformer faulted/mechanical | 0 | DEN
| 79 | 2012-07-23 04:56 | Foreign Object | Bird contact | 0 | DEN
| 79 | 2012-08-05 08:40 | Customer Contact | Vehicle contact | 0 | DEN
| 79 | 2012-08-08 13:43 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-08-11 14:41 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2012-08-12 13:08 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2012-08-13 13:24 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-08-15 13:38 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-08-30 12:43 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2012-10-04 09:26 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-10-06 16:13 | Undetermined | Undetermined | 0 | DEN
| 79 | 2012-12-10 06:27 | Equipment | Transformer faulted/mechanical | 0 | DEN
| 79 | 2012-12-13 13:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2013-01-26 07:00 | Undetermined | Undetermined | 0 | DEN
| 79 | 2013-02-08 16:07 | Undetermined | Undetermined | 0 | DEN
| 79 | 2013-02-12 02:17 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2013-02-16 00:54 | Equipment | Insulator/pin failure/wire floating | 0 | DEN
| 79 | 2013-02-20 03:22 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2013-02-21 18:21 | Weather | Ice or snow/Equipment failure | 0 | DEN
| 79 | 2013-04-05 04:58 | Undetermined | Undetermined | 0 | DEN
| 79 | 2013-07-06 09:35 | Undetermined | Undetermined | 1 | DEN
| 79 | 2013-07-21 19:44 | Undetermined | Undetermined | 0 | DEN
| 79 | 2013-08-04 15:28 | Equipment | Conductor failure/wire down | 0 | DEN
| 79 | 2013-09-04 12:56 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2013-09-07 12:25 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2014-01-15 08:24 | Undetermined | Undetermined | 0 | DEN
| 79 | 2014-02-13 02:53 | Undetermined | Undetermined | 0 | DEN
| 79 | 2014-03-09 11:30 | Tree Contact | Tree fell on line | 0 | DEN
| 79 | 2014-03-09 18:34 | Tree Contact | Tree fell on line | 0 | DEN
| 79 | 2014-03-26 18:10 | Equipment | Conductor failure/wire down | 0 | DEN
| 79 | 2014-03-30 08:10 | Undetermined | Undetermined | 0 | DEN
| 79 | 2014-04-28 19:30 | Equipment | Conductor contact/wire slap | 0 | DEN
| 79 | 2014-04-30 01:17 | Weather | Tree fell on line due to storm/wind | 0 | DEN
| 79 | 2014-04-30 06:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2014-05-01 03:15 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2014-05-13 09:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2014-05-13 13:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2014-05-14 06:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN
| 79 | 2014-07-29 06:43 | Undetermined | Undetermined | 0 | DEN
| 79 | 2014-08-03 12:30 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2014-08-12 13:37 | Weather | Lightning Arrester/Transformer failure | 0 | DEN
| 79 | 2014-08-21 17:49 | Undetermined | Undetermined | 0 | DEN
| 79 | 2014-10-18 10:01 | Undetermined | Undetermined | 0 | DEN
| 79 | 2014-11-05 20:38 | Weather | Wind - wires slap/pole down | 0 | DEN
| 79 | 2015-01-01 23:58 | Equipment | Conductor failure/wire down | 0 | DEN
| 79 | 2015-01-24 07:44 | Equipment | Conductor contact/wire slap | 0 | DEN
| 79 | 2015-01-24 08:31 | Equipment | Arrester (lightning) failure | 0 | DEN
| 79 | 2015-03-09 00:21 | Customer Contact | Vehicle contact | 0 | DEN
| 81 | 2013-06-27 07:44 | Equipment | Transformer faulted/mechanical | 0 | KSAN
| 907 | 2005-03-08 11:10 | Foreign Object | Foreign object in distribution line | 0 | VLC
| 907 | 2005-03-15 09:51 | Foreign Object | Bird contact | 0 | VLC
| 907 | 2005-04-29 10:43 | Undetermined | Undetermined | 0 | VLC
| 907 | 2005-05-19 06:56 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC
| 907 | 2005-07-28 12:56 | Foreign Object | Foreign object in distribution line | 0 | VLC
| 907 | 2005-09-20 06:36 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 907 | 2005-12-07 12:56 | Undetermined | Undetermined | 0 | VLC
| 907 | 2006-01-11 10:39 | Customer Contact | Heavy equp contact/digin | 0 | VLC
| 907 | 2006-03-29 09:45 | Undetermined | Undetermined | 0 | VLC
| 907 | 2006-03-29 18:31 | Equipment | Conductor failure/wire down | 0 | VLC
| 907 | 2006-04-23 07:46 | Undetermined | Undetermined | 0 | VLC
| 907 | 2006-08-28 11:53 | Equipment | Conductor failure/wire down | 0 | VLC
| 907 | 2006-09-26 10:44 | Equipment | Transformer faulted/mechanical | 0 | VLC
| 907 | 2007-02-06 07:56 | Customer Contact | Vehicle contact | 0 | VLC
| 907 | 2007-05-16 05:45 | Foreign Object | Bird contact | 0 | VLC
| 907 | 2007-06-08 13:54 | Foreign Object | Animal contact | 0 | VLC
| 907 | 2007-10-30 08:56 | Customer Contact | Heavy equp contact/digin | 0 | VLC
| 907 | 2007-12-27 22:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC
| 907 | 2008-01-21 11:37 | Undetermined | Undetermined | 0 | VLC
| 907 | 2008-05-22 13:45 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 907 | 2008-05-23 15:51 | Undetermined | Undetermined | 0 | VLC
| 907 | 2008-12-12 08:28 | Equipment | Fuse holder/fuse cabinet failed | 0 | VLC
| 907 | 2009-06-03 23:53 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 907 | 2010-01-06 21:01 | Equipment | Fuse overloaded/inadequate fuse size | 0 | VLC
| 907 | 2010-09-30 12:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 907 | 2011-10-07 09:48 | Undetermined | Undetermined | 0 | VLC
| 907 | 2012-09-10 14:48 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 907 | 2012-10-11 11:45 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 907 | 2013-01-08 07:14 | Equipment | Fuse overloaded/inadequate fuse size | 0 | VLC
| 907 | 2013-02-08 11:45 | Customer Contact | Vehicle contact | 0 | VLC
| 907 | 2013-10-22 08:50 | Equipment | Transformer faulted/mechanical | 0 | VLC
| 907 | 2014-06-24 12:47 | Tree Contact | Tree fell on line | 0 | VLC
| 907 | 2014-08-23 01:23 | Undetermined | Undetermined | 0 | VLC
| 908 | 2005-02-10 21:40 | Undetermined | Undetermined | 0 | HID
| 908 | 2005-04-01 04:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2005-04-01 06:08 | Weather | Tree contact due to storm/high wind | 0 | HID
| 908 | 2005-06-12 16:49 | Foreign Object | Foreign object in distribution line | 0 | HID
| 908 | 2005-07-03 15:05 | Tree Contact | Tree fell on line | 1 | HID
| 908 | 2005-07-23 02:19 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2005-07-23 04:53 | Weather | Wind - wires slap/pole down | 0 | HID
| 908 | 2005-07-23 04:53 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2005-07-23 07:37 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2005-07-23 11:17 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2005-09-20 06:24 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2005-09-21 03:00 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2005-12-21 15:09 | Undetermined | Undetermined | 0 | HID
| 908 | 2005-12-24 12:54 | Foreign Object | Bird contact | 0 | HID
| 908 | 2006-01-02 09:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2006-01-07 15:11 | Equipment | Transformer faulted/mechanical | 0 | HID
| 908 | 2006-01-25 11:27 | Undetermined | Undetermined | 0 | HID
| 908 | 2006-05-16 07:06 | Undetermined | Undetermined | 0 | HID
| 908 | 2006-07-10 18:43 | Undetermined | Undetermined | 1 | HID
| 908 | 2006-09-20 18:47 | Foreign Object | Bird contact | 0 | HID
| 908 | 2006-10-13 10:28 | Undetermined | Undetermined | 0 | HID
| 908 | 2006-12-03 08:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2007-01-30 07:14 | Undetermined | Undetermined | 0 | HID
| 908 | 2007-03-04 09:49 | Weather | Palm tree contact due to storm/wind | 0 | HID
| 908 | 2007-04-04 17:39 | Equipment | Cutout failure | 0 | HID
| 908 | 2007-06-12 00:50 | Tree Contact | Tree contact | 0 | HID
| 908 | 2007-06-27 05:38 | Foreign Object | Bird contact | 0 | HID
| 908 | 2007-06-27 09:52 | Foreign Object | Bird contact | 0 | HID
| 908 | 2007-07-04 15:40 | Foreign Object | Bird contact | 1 | HID
| 908 | 2007-07-26 09:18 | Equipment | Crossarm failure | 0 | HID
| 908 | 2007-10-22 04:18 | Undetermined | Undetermined | 0 | HID
| 908 | 2007-12-18 16:19 | Undetermined | Undetermined | 0 | HID
| 908 | 2007-12-26 22:03 | Undetermined | Undetermined | 0 | HID
| 908 | 2008-01-08 09:11 | Undetermined | Undetermined | 0 | HID
| 908 | 2008-01-16 18:58 | Weather | Wind - wires slap/pole down | 0 | HID
| 908 | 2008-01-25 13:26 | Undetermined | Undetermined | 0 | HID
| 908 | 2008-02-05 07:02 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HID
| 908 | 2008-02-17 10:10 | Equipment | Conductor failure/wire down | 0 | HID
| 908 | 2008-03-24 14:10 | Undetermined | Undetermined | 0 | HID
| 908 | 2008-05-22 20:31 | Equipment | Cutout failure | 0 | HID
| 908 | 2008-06-18 19:19 | Undetermined | Undetermined | 0 | HID
| 908 | 2008-06-21 23:07 | Undetermined | Undetermined | 0 | HID
| 908 | 2009-04-16 16:16 | Customer Contact | Vehicle contact | 0 | HID
| 908 | 2009-05-21 19:00 | Undetermined | Undetermined | 0 | HID
| 908 | 2009-06-29 14:50 | Foreign Object | Bird contact | 0 | HID
| 908 | 2009-07-14 12:15 | Equipment | Fuse overloaded/inadequate fuse size | 1 | HID
| 908 | 2009-07-27 13:47 | Undetermined | Undetermined | 0 | HID
| 908 | 2009-08-19 14:31 | Customer Contact | Vehicle contact | 0 | HID
| 908 | 2009-08-20 22:04 | Equipment | Recloser/breaker faulted/mechanical | 0 | HID
| 908 | 2009-12-06 02:12 | Undetermined | Undetermined | 0 | HID
| 908 | 2009-12-23 02:13 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HID
| 908 | 2010-01-20 17:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2010-01-21 16:10 | Equipment | Fuse holder/fuse cabinet failed | 0 | HID
| 908 | 2010-05-15 10:11 | Foreign Object | Aircraft | 0 | HID
| 908 | 2010-10-19 02:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2010-10-19 02:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2010-10-22 14:31 | Customer Contact | Vehicle contact | 0 | HID
| 908 | 2010-12-22 04:11 | Weather | Wind - wires slap/pole down | 0 | HID
| 908 | 2011-03-24 08:53 | Equipment | Transformer faulted/mechanical | 0 | HID
| 908 | 2011-04-25 07:09 | Undetermined | Undetermined | 0 | HID
| 908 | 2011-09-09 04:01 | Equipment | Transformer faulted/mechanical | 0 | HID
| 908 | 2011-10-05 20:44 | Equipment | Arrester (lightning) failure | 0 | HID
| 908 | 2011-11-02 08:09 | Weather | Tree fell on line due to storm/wind | 0 | HID
| 908 | 2011-11-15 15:50 | Customer Contact | Vehicle contact | 0 | HID
| 908 | 2012-01-09 16:46 | Equipment | Insulator/pin failure/wire floating | 0 | HID
| 908 | 2012-05-13 12:57 | Equipment | Cutout failure | 0 | HID
| 908 | 2012-06-01 16:41 | Undetermined | Undetermined | 0 | HID
| 908 | 2012-06-27 10:26 | Foreign Object | Bird contact | 0 | HID
| 908 | 2012-09-09 15:59 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2012-09-09 16:11 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2012-09-09 16:11 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2012-09-09 16:11 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2012-10-11 11:23 | Weather | Lightning Arrester/Transformer failure | 0 | HID
| 908 | 2012-11-30 19:08 | Equipment | Transformer faulted/mechanical | 0 | HID
| 908 | 2013-04-22 06:28 | Equipment | Conductor failure/wire down | 0 | HID
| 908 | 2013-07-21 20:31 | Foreign Object | Bird contact | 0 | HID
| 908 | 2013-10-10 03:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID
| 908 | 2013-12-23 12:29 | Foreign Object | Bird contact | 0 | HID
| 908 | 2013-12-23 17:42 | Foreign Object | Bird contact | 0 | HID
| 908 | 2014-02-05 09:43 | Foreign Object | Bird contact | 0 | HID
| 908 | 2014-02-06 22:44 | Equipment | Transformer faulted/mechanical | 0 | HID
| 908 | 2014-05-30 09:37 | Equipment | Arrester (lightning) failure | 0 | HID
| 908 | 2014-07-02 15:40 | Undetermined | Undetermined | 1 | HID
| 908 | 2014-10-23 10:03 | Undetermined | Undetermined | 0 | HID
| 908 | 2014-12-03 07:29 | Equipment | Transformer faulted/mechanical | 0 | HID
| 908 | 2014-12-12 12:46 | Undetermined | Undetermined | 0 | HID
| 908 | 2015-02-24 06:47 | Equipment | Cutout failure | 0 | HID
| 909 | 2005-01-22 07:20 | Undetermined | Undetermined | 0 | VLC
| 909 | 2006-03-01 10:02 | Equipment | Cutout failure | 0 | VLC
| 909 | 2006-03-29 16:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2006-06-06 05:41 | Undetermined | Undetermined | 0 | VLC
| 909 | 2006-07-06 15:05 | Foreign Object | Foreign object in distribution line | 1 | VLC
| 909 | 2006-08-13 13:05 | Foreign Object | Foreign object in distribution line | 0 | VLC
| 909 | 2006-10-31 10:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC
| 909 | 2006-12-10 14:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2007-03-03 13:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2007-03-03 16:52 | Customer Contact | Vehicle contact | 0 | VLC
| 909 | 2007-03-04 11:35 | Customer Contact | Vehicle contact | 0 | VLC
| 909 | 2007-06-08 16:43 | Foreign Object | Animal contact | 0 | VLC
| 909 | 2007-10-22 12:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2007-10-23 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2007-10-23 16:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2007-12-05 08:12 | Undetermined | Undetermined | 0 | VLC
| 909 | 2007-12-07 06:04 | Equipment | Transformer faulted/mechanical | 0 | VLC
| 909 | 2007-12-31 20:21 | Weather | Wind - wires slap/pole down | 0 | VLC
| 909 | 2008-01-01 08:46 | Weather | Wind - wires slap/pole down | 0 | VLC
| 909 | 2009-09-21 10:58 | Foreign Object | Foreign object in distribution line | 0 | VLC
| 909 | 2009-10-13 01:25 | Foreign Object | Foreign object in distribution line | 0 | VLC
| 909 | 2009-10-29 22:56 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC
| 909 | 2009-12-20 11:11 | Customer Contact | Vehicle contact | 0 | VLC
| 909 | 2010-01-21 15:49 | Weather | Wind - wires slap/pole down | 0 | VLC
| 909 | 2010-04-15 13:04 | Equipment | Conductor contact/wire slap | 0 | VLC
| 909 | 2010-05-28 16:44 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC
| 909 | 2010-06-27 13:38 | Foreign Object | Foreign object in distribution line | 0 | VLC
| 909 | 2010-08-25 14:08 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 909 | 2010-11-30 14:41 | Customer Contact | Heavy equp contact/digin | 0 | VLC
| 909 | 2011-01-23 08:11 | Weather | Wind - wires slap/pole down | 0 | VLC
| 909 | 2011-05-28 17:34 | Undetermined | Undetermined | 0 | VLC
| 909 | 2011-08-04 14:43 | Undetermined | Undetermined | 0 | VLC
| 909 | 2012-01-08 13:00 | Customer Contact | Line fault/tree trimming | 0 | VLC
| 909 | 2012-03-14 11:21 | Foreign Object | Bird contact | 0 | VLC
| 909 | 2012-04-13 18:07 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 909 | 2012-07-18 14:30 | Foreign Object | Bird contact | 0 | VLC
| 909 | 2012-09-10 19:18 | Equipment | Pole broke/rotted/on fire | 0 | VLC
| 909 | 2012-12-13 14:29 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 909 | 2013-03-30 18:02 | Equipment | Transformer faulted/mechanical | 0 | VLC
| 909 | 2013-04-23 15:05 | Foreign Object | Bird contact | 0 | VLC
| 909 | 2013-10-09 22:43 | Weather | Lightning Arrester/Transformer failure | 0 | VLC
| 909 | 2013-10-12 12:12 | Customer Contact | Vehicle contact | 0 | VLC
| 909 | 2014-03-09 12:43 | Equipment | Insulator/pin failure/wire floating | 0 | VLC
| 909 | 2014-05-14 08:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC
| 909 | 2014-12-03 01:55 | Equipment | Transformer faulted/mechanical | 0 | VLC
| 92 | 2005-10-23 07:21 | Customer Contact | Vehicle contact | 0 | OTY
| 92 | 2007-08-25 09:48 | Undetermined | Undetermined | 0 | OTY
| 92 | 2008-02-20 09:28 | Foreign Object | Foreign object in distribution line | 0 | OTY
| 92 | 2008-04-29 01:37 | Customer Contact | Vehicle contact | 0 | OTY
| 92 | 2008-10-03 02:02 | Customer Contact | Vehicle contact | 0 | OTY
| 92 | 2009-09-27 15:34 | Foreign Object | Foreign object in distribution line | 0 | OTY
| 92 | 2009-12-11 16:41 | Equipment | Capacitor failure | 0 | OTY
| 92 | 2010-01-19 13:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY
| 92 | 2013-09-23 08:40 | Customer Contact | Vehicle contact | 0 | OTY
| 920 | 2005-03-31 09:18 | Weather | Tree fell on line due to storm/wind | 0 | SYC
| 920 | 2005-05-15 00:29 | Undetermined | Undetermined | 0 | SYC
| 920 | 2005-07-23 09:36 | Weather | Lightning Arrester/Transformer failure | 0 | SYC
| 920 | 2006-02-22 12:12 | Customer Contact | Heavy equp contact/digin | 0 | SYC
| 920 | 2006-03-10 22:47 | Weather | Wind - wires slap/pole down | 0 | SYC
| 920 | 2006-04-11 15:23 | Undetermined | Undetermined | 0 | SYC
| 920 | 2006-04-13 13:24 | Undetermined | Undetermined | 0 | SYC
| 920 | 2006-07-31 08:44 | Equipment | Capacitor failure | 0 | SYC
| 920 | 2006-09-01 13:13 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SYC
| 920 | 2006-09-20 07:57 | Undetermined | Undetermined | 0 | SYC
| 920 | 2006-12-02 18:39 | Weather | Tree fell on line due to storm/wind | 0 | SYC
| 920 | 2007-01-06 09:38 | Weather | Tree fell on line due to storm/wind | 0 | SYC
| 920 | 2007-09-01 15:08 | Equipment | Fuse overloaded/inadequate fuse size | 0 | SYC
| 920 | 2008-09-23 01:52 | Customer Contact | Vehicle contact | 0 | SYC
| 920 | 2008-12-16 16:08 | Weather | Tree fell on line due to storm/wind | 0 | SYC
| 920 | 2009-02-25 06:22 | Foreign Object | Bird contact | 0 | SYC
| 920 | 2009-05-14 00:06 | Undetermined | Undetermined | 0 | SYC
| 920 | 2010-09-30 17:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SYC
| 920 | 2012-03-26 06:46 | Undetermined | Undetermined | 0 | SYC
| 920 | 2012-06-11 13:58 | Foreign Object | Bird contact | 0 | SYC
| 920 | 2013-01-31 10:57 | Customer Contact | Heavy equp contact/digin | 0 | SYC
| 920 | 2013-09-16 07:19 | Tree Contact | Tree fell on line | 0 | SYC
| 920 | 2015-03-13 17:06 | Equipment | Arrester (lightning) failure | 0 | SYC
| 970 | 2006-02-12 12:26 | Undetermined | Undetermined | 0 | RAM
| 970 | 2007-05-06 03:21 | Undetermined | Undetermined | 0 | RAM
| 970 | 2010-04-06 09:12 | Undetermined | Undetermined | 0 | RAM
| 971 | 2005-01-07 15:47 | Customer Contact | Vehicle contact | 0 | MGR
| 971 | 2005-06-14 11:57 | Customer Contact | Heavy equp contact/digin | 0 | MGR
| 971 | 2005-07-30 21:12 | Equipment | Crossarm failure | 0 | MGR
| 971 | 2005-10-19 11:38 | Undetermined | Undetermined | 0 | MGR
| 971 | 2005-11-04 19:21 | Undetermined | Undetermined | 0 | MGR
| 971 | 2005-11-06 06:09 | Customer Contact | Vehicle contact | 0 | MGR
| 971 | 2006-06-29 16:49 | Tree Contact | Tree fell on line | 0 | MGR
| 971 | 2006-11-01 12:27 | Undetermined | Undetermined | 0 | MGR
| 971 | 2007-02-24 17:20 | Equipment | Transformer faulted/mechanical | 0 | MGR
| 971 | 2007-08-05 14:00 | Foreign Object | Foreign object in distribution line | 0 | MGR
| 971 | 2007-08-22 19:33 | Customer Contact | Line fault/tree trimming | 0 | MGR
| 971 | 2008-01-06 01:31 | Undetermined | Undetermined | 0 | MGR
| 971 | 2008-01-07 07:38 | Weather | Wind - wires slap/pole down | 0 | MGR
| 971 | 2008-05-21 10:03 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2008-06-06 08:57 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2008-06-28 04:18 | Customer Contact | Vehicle contact | 0 | MGR
| 971 | 2008-09-06 05:35 | Customer Contact | Vehicle contact | 0 | MGR
| 971 | 2008-09-12 08:54 | Equipment | Crossarm failure | 0 | MGR
| 971 | 2008-11-26 19:11 | Equipment | Arrester (lightning) failure | 0 | MGR
| 971 | 2009-02-09 12:50 | Weather | Wind - wires slap/pole down | 0 | MGR
| 971 | 2009-03-16 10:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR
| 971 | 2009-05-25 19:33 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2009-08-30 11:02 | Equipment | Transformer faulted/mechanical | 0 | MGR
| 971 | 2009-09-06 08:30 | Equipment | Conductor failure/wire down | 0 | MGR
| 971 | 2010-01-19 17:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGR
| 971 | 2010-03-12 06:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR
| 971 | 2010-08-07 09:38 | Foreign Object | Damage by gunshot | 0 | MGR
| 971 | 2010-09-30 12:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGR
| 971 | 2010-12-05 07:55 | Customer Contact | Vehicle contact | 0 | MGR
| 971 | 2010-12-23 02:09 | Foreign Object | Animal contact | 0 | MGR
| 971 | 2011-01-25 12:07 | Customer Contact | Vehicle contact | 0 | MGR
| 971 | 2011-03-22 10:20 | Equipment | Crossarm failure | 0 | MGR
| 971 | 2011-05-20 18:02 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2011-05-29 03:38 | Undetermined | Undetermined | 0 | MGR
| 971 | 2012-02-04 14:58 | Undetermined | Undetermined | 0 | MGR
| 971 | 2012-03-13 23:51 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR
| 971 | 2012-03-22 07:10 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2012-08-05 06:38 | Foreign Object | Animal contact | 0 | MGR
| 971 | 2012-08-11 12:15 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2012-09-20 19:42 | Foreign Object | Damage by gunshot | 0 | MGR
| 971 | 2012-10-06 15:07 | Undetermined | Undetermined | 0 | MGR
| 971 | 2012-12-23 16:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGR
| 971 | 2013-04-29 09:15 | Foreign Object | Bird contact | 0 | MGR
| 971 | 2013-07-04 07:57 | Foreign Object | Bird contact | 1 | MGR
| 971 | 2014-02-18 17:01 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR
| 971 | 2014-03-02 08:18 | Equipment | Capacitor failure | 0 | MGR
| 971 | 2014-06-05 19:56 | Foreign Object | Foreign object in distribution line | 0 | MGR
| 971 | 2014-07-10 09:21 | Foreign Object | Bird contact | 1 | MGR
| 971 | 2014-08-31 17:15 | Undetermined | Undetermined | 0 | MGR
| 971 | 2015-03-10 11:55 | Customer Contact | Vehicle contact | 0 | MGR
| 972 | 2005-01-02 14:33 | Equipment | Conductor failure/wire down | 0 | HVY
| 972 | 2005-01-10 07:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2005-09-19 16:23 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2005-09-19 17:03 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2005-11-21 14:47 | Equipment | Fuse overloaded/inadequate fuse size | 0 | HVY
| 972 | 2006-01-23 08:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY
| 972 | 2006-06-27 09:30 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2006-09-03 13:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2006-11-06 09:20 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2006-12-11 10:37 | Foreign Object | Bird contact | 0 | HVY
| 972 | 2006-12-17 22:52 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2007-03-04 07:35 | Undetermined | Undetermined | 0 | HVY
| 972 | 2007-03-12 01:02 | Foreign Object | Foreign object in distribution line | 0 | HVY
| 972 | 2007-04-24 14:23 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY
| 972 | 2007-06-16 18:25 | Undetermined | Undetermined | 0 | HVY
| 972 | 2007-10-21 20:27 | Weather | Wind - wires slap/pole down | 0 | HVY
| 972 | 2007-10-22 06:31 | Weather | Wind - wires slap/pole down | 0 | HVY
| 972 | 2007-10-22 18:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2007-11-05 09:00 | Equipment | Pole broke/rotted/on fire | 0 | HVY
| 972 | 2007-11-30 07:34 | Equipment | Arrester (lightning) failure | 0 | HVY
| 972 | 2008-01-02 12:53 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2008-01-05 07:12 | Equipment | Cutout failure | 0 | HVY
| 972 | 2008-02-23 11:49 | Undetermined | Undetermined | 0 | HVY
| 972 | 2008-08-29 20:18 | Undetermined | Undetermined | 0 | HVY
| 972 | 2008-09-01 21:56 | Undetermined | Undetermined | 0 | HVY
| 972 | 2008-09-09 13:15 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2008-12-19 07:35 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2008-12-25 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2009-04-19 02:13 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2009-05-20 06:44 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY
| 972 | 2009-08-08 07:54 | Foreign Object | Bird contact | 0 | HVY
| 972 | 2009-09-02 15:43 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2009-11-28 08:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2009-12-07 11:01 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2009-12-07 14:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2009-12-07 17:02 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2009-12-08 07:52 | Weather | Ice or snow/Equipment failure | 0 | HVY
| 972 | 2009-12-22 08:22 | Equipment | Insulator/pin failure/wire floating | 0 | HVY
| 972 | 2010-01-19 14:26 | Weather | Tree fell on line due to storm/wind | 0 | HVY
| 972 | 2010-01-19 19:56 | Weather | Wind - wires slap/pole down | 0 | HVY
| 972 | 2010-01-21 17:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2010-04-07 09:41 | Equipment | Insulator/pin failure/wire floating | 0 | HVY
| 972 | 2010-05-20 16:30 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2010-09-27 21:00 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2011-01-10 11:25 | Foreign Object | Foreign object in distribution line | 0 | HVY
| 972 | 2011-04-01 18:40 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2011-05-01 14:34 | Undetermined | Undetermined | 0 | HVY
| 972 | 2011-08-05 05:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY
| 972 | 2011-11-30 21:41 | Undetermined | Undetermined | 0 | HVY
| 972 | 2011-12-12 14:21 | Weather | Wind - wires slap/pole down | 0 | HVY
| 972 | 2012-01-24 05:12 | Undetermined | Undetermined | 0 | HVY
| 972 | 2012-03-08 03:25 | Equipment | Conductor failure/wire down | 0 | HVY
| 972 | 2012-10-12 05:45 | Weather | Lightning Arrester/Transformer failure | 0 | HVY
| 972 | 2012-11-24 11:30 | Equipment | Transformer faulted/mechanical | 0 | HVY
| 972 | 2013-04-17 14:32 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY
| 972 | 2013-04-30 08:20 | Undetermined | Undetermined | 0 | HVY
| 972 | 2013-08-09 11:10 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY
| 972 | 2013-10-06 10:06 | Equipment | Cutout failure | 0 | HVY
| 972 | 2013-10-10 00:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2014-02-28 12:42 | Weather | Wind - wires slap/pole down | 0 | HVY
| 972 | 2014-04-29 04:31 | Equipment | Regulator faulted/mechanical | 0 | HVY
| 972 | 2014-04-29 17:56 | Equipment | Regulator faulted/mechanical | 0 | HVY
| 972 | 2014-04-30 11:13 | Undetermined | Undetermined | 0 | HVY
| 972 | 2014-05-06 22:17 | Equipment | Crossarm failure | 0 | HVY
| 972 | 2014-05-13 10:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2014-05-14 08:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY
| 972 | 2014-07-06 08:43 | Foreign Object | Bird contact | 1 | HVY
| 972 | 2014-07-06 11:31 | Undetermined | Undetermined | 1 | HVY
| 972 | 2014-07-10 22:53 | Equipment | Insulator/pin failure/wire floating | 1 | HVY
| 972 | 2014-08-29 04:43 | Undetermined | Undetermined | 0 | HVY
| 972 | 2014-08-29 14:49 | Equipment | Conductor failure/wire down | 0 | HVY
| 972 | 2014-09-05 06:04 | Customer Contact | Vehicle contact | 0 | HVY
| 972 | 2014-12-03 03:53 | Equipment | Transformer faulted/mechanical | 0 | HVY
| 972 | 2015-01-24 12:00 | Undetermined | Undetermined | 0 | HVY
| 972 | 2015-01-25 09:02 | Equipment | Conductor contact/wire slap | 0 | HVY
| 972 | 2015-02-08 09:12 | Foreign Object | Bird contact | 0 | HVY
| 972 | 2015-03-01 21:35 | Equipment | Transformer faulted/mechanical | 0 | HVY
| 973 | 2005-02-11 06:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2006-01-02 14:43 | Weather | Wind - wires slap/pole down | 0 | SPP
| 973 | 2006-01-24 05:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2006-07-14 08:15 | Undetermined | Undetermined | 1 | SPP
| 973 | 2006-08-07 12:25 | Undetermined | Undetermined | 0 | SPP
| 973 | 2007-01-10 09:12 | Equipment | Transformer faulted/mechanical | 0 | SPP
| 973 | 2007-04-20 15:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2007-08-30 17:02 | Undetermined | Undetermined | 0 | SPP
| 973 | 2007-10-13 03:29 | Equipment | Arrester (lightning) failure | 0 | SPP
| 973 | 2007-10-13 10:35 | Undetermined | Undetermined | 0 | SPP
| 973 | 2009-03-07 13:45 | Undetermined | Undetermined | 0 | SPP
| 973 | 2009-04-09 16:47 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SPP
| 973 | 2009-04-22 10:26 | Undetermined | Undetermined | 0 | SPP
| 973 | 2009-09-02 15:02 | Weather | Lightning Arrester/Transformer failure | 0 | SPP
| 973 | 2010-01-19 14:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2010-01-21 07:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2010-01-21 12:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2010-09-25 21:20 | Equipment | Transformer faulted/mechanical | 0 | SPP
| 973 | 2010-09-30 12:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2010-10-20 17:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SPP
| 973 | 2011-03-23 22:00 | Foreign Object | Foreign object in distribution line | 0 | SPP
| 973 | 2012-03-19 07:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2012-05-09 19:54 | Undetermined | Undetermined | 0 | SPP
| 973 | 2012-10-11 14:27 | Equipment | Arrester (lightning) failure | 0 | SPP
| 973 | 2013-03-12 15:53 | Equipment | Crossarm failure | 0 | SPP
| 973 | 2013-09-04 16:32 | Equipment | Recloser/breaker faulted/mechanical | 0 | SPP
| 973 | 2014-02-28 12:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2014-02-28 16:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2014-04-26 09:21 | Undetermined | Undetermined | 0 | SPP
| 973 | 2014-05-14 19:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP
| 973 | 2014-08-03 13:06 | Weather | Lightning Arrester/Transformer failure | 0 | SPP
| 974 | 2005-02-03 19:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA
| 974 | 2005-11-15 12:26 | Undetermined | Undetermined | 0 | BNA
| 974 | 2006-10-31 21:21 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2006-12-27 07:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA
| 974 | 2006-12-27 09:59 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2007-11-23 05:56 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2008-09-04 03:23 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2009-10-21 15:57 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2010-03-03 11:18 | Undetermined | Undetermined | 0 | BNA
| 974 | 2010-09-30 12:29 | Weather | Lightning Arrester/Transformer failure | 0 | BNA
| 974 | 2010-10-08 10:06 | Undetermined | Undetermined | 0 | BNA
| 974 | 2010-11-02 11:18 | Foreign Object | Bird contact | 0 | BNA
| 974 | 2011-05-22 14:44 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2011-09-07 18:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA
| 974 | 2012-03-18 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA
| 974 | 2012-03-18 12:42 | Weather | Wind - wires slap/pole down | 0 | BNA
| 974 | 2012-03-18 15:13 | Weather | Wind - wires slap/pole down | 0 | BNA
| 974 | 2012-03-19 07:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA
| 974 | 2012-10-31 17:32 | Undetermined | Undetermined | 0 | BNA
| 974 | 2013-08-24 07:43 | Equipment | Capacitor failure | 0 | BNA
| 974 | 2014-07-25 09:06 | Weather | Lightning Arrester/Transformer failure | 0 | BNA
| 974 | 2014-08-23 07:16 | Customer Contact | Vehicle contact | 0 | BNA
| 974 | 2014-10-11 03:52 | Equipment | Conductor contact/wire slap | 0 | BNA
| 974 | 2015-01-25 10:25 | Undetermined | Undetermined | 0 | BNA
| 974 | 2015-01-25 10:32 | Undetermined | Undetermined | 0 | BNA
| 974 | 2015-01-25 10:51 | Undetermined | Undetermined | 0 | BNA
| 974 | 2015-02-15 05:55 | Customer Contact | Vehicle contact | 0 | BNA
| 984 | 2005-03-01 10:04 | Undetermined | Undetermined | 0 | CAP
| 984 | 2005-05-31 15:54 | Foreign Object | Bird contact | 0 | CAP
| 984 | 2005-07-08 13:42 | Equipment | Pole broke/rotted/on fire | 1 | CAP
| 984 | 2006-01-03 09:00 | Undetermined | Undetermined | 0 | CAP
| 984 | 2006-02-22 10:33 | Undetermined | Undetermined | 0 | CAP
| 984 | 2006-03-16 18:20 | Equipment | Conductor failure/wire down | 0 | CAP
| 984 | 2006-04-20 10:30 | Undetermined | Undetermined | 0 | CAP
| 984 | 2006-04-22 07:19 | Undetermined | Undetermined | 0 | CAP
| 984 | 2006-07-08 08:56 | Customer Contact | Vehicle contact | 1 | CAP
| 984 | 2006-11-20 01:38 | Undetermined | Undetermined | 0 | CAP
| 984 | 2007-01-21 16:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CAP
| 984 | 2007-02-24 13:09 | Undetermined | Undetermined | 0 | CAP
| 984 | 2007-03-16 12:33 | Foreign Object | Bird contact | 0 | CAP
| 984 | 2007-05-12 11:21 | Undetermined | Undetermined | 0 | CAP
| 984 | 2007-11-28 13:17 | Equipment | Conductor failure/wire down | 0 | CAP
| 984 | 2007-12-19 06:53 | Weather | Lightning Arrester/Transformer failure | 0 | CAP
| 984 | 2008-09-29 14:05 | Weather | Lightning Arrester/Transformer failure | 0 | CAP
| 984 | 2009-11-16 11:25 | Customer Contact | Heavy equp contact/digin | 0 | CAP
| 984 | 2010-01-06 10:18 | Equipment | Pole broke/rotted/on fire | 0 | CAP
| 984 | 2010-03-21 12:23 | Foreign Object | Bird contact | 0 | CAP
| 984 | 2010-05-28 13:45 | Equipment | Transformer faulted/mechanical | 0 | CAP
| 984 | 2010-09-26 13:10 | Customer Contact | Vehicle contact | 0 | CAP
| 984 | 2010-10-19 07:39 | Weather | Lightning Arrester/Transformer failure | 0 | CAP
| 984 | 2011-09-29 05:26 | Undetermined | Undetermined | 0 | CAP
| CTL1 | 2008-09-08 07:07 | Undetermined | Undetermined | 0 | PAM
| CTL1 | 2009-01-25 16:37 | Weather | Ice or snow/Equipment failure | 0 | PAM
| CTL1 | 2011-02-27 12:02 | Weather | Tree fell on line due to storm/wind | 0 | PAM
| CTL1 | 2011-12-10 15:04 | Foreign Object | Foreign object in distribution line | 0 | PAM
| CTL1 | 2014-06-27 23:51 | Equipment | Fuse overloaded/inadequate fuse size | 0 | PAM
| RB1 | 2007-07-02 14:30 | Undetermined | Undetermined | 1 | RNB
| RB1 | 2007-07-02 14:30 | Undetermined | Undetermined | 1 | RNB
| RB1 | 2009-12-02 06:29 | Equipment | Conductor failure/wire down | 0 | RNB
| RB1 | 2009-12-02 06:29 | Equipment | Conductor failure/wire down | 0 | RNB
| RB1 | 2010-09-27 12:47 | Foreign Object | Foreign object in distribution line | 0 | RNB
| RB1 | 2010-09-27 12:47 | Foreign Object | Foreign object in distribution line | 0 | RNB
| RB1 | 2011-07-05 02:29 | Undetermined | Undetermined | 1 | RNB
| RB1 | 2011-07-05 02:29 | Undetermined | Undetermined | 1 | RNB
| RB1 | 2011-09-08 13:10 | Undetermined | Undetermined | 0 | RNB
| RB1 | 2011-09-08 13:10 | Undetermined | Undetermined | 0 | RNB
| RB1 | 2012-03-03 22:03 | Customer Contact | Vehicle contact | 0 | RNB
| RB1 | 2012-03-03 22:03 | Customer Contact | Vehicle contact | 0 | RNB
| RB1 | 2013-02-01 05:39 | Equipment | Conductor contact/wire slap | 0 | RNB
| RB1 | 2013-02-01 05:39 | Equipment | Conductor contact/wire slap | 0 | RNB
| RB1 | 2013-02-01 07:13 | Equipment | Conductor contact/wire slap | 0 | RNB
| RB1 | 2013-02-01 07:13 | Equipment | Conductor contact/wire slap | 0 | RNB
| RB1 | 2013-06-28 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RNB
| RB1 | 2013-06-28 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RNB
| RB1 | 2014-01-23 02:43 | Equipment | Fuse overloaded/inadequate fuse size | 0 | RNB
| RB1 | 2014-01-23 02:43 | Equipment | Fuse overloaded/inadequate fuse size | 0 | RNB
| TM1 | 2005-05-07 21:39 | Undetermined | Undetermined | 0 | PTM
| TM1 | 2007-09-27 06:16 | Customer Contact | Vehicle contact | 0 | PTM
| TM1 | 2010-01-22 07:31 | Equipment | Circuit Breaker/Recloser Failure (Sub) | 0 | PTM
| TM1 | 2010-01-23 07:57 | Equipment | Circuit Breaker/Recloser Failure (Sub) | 0 | PTM
| TM1 | 2010-07-14 11:01 | Undetermined | Undetermined | 1 | PTM
| TM1 | 2010-07-15 09:57 | Undetermined | Undetermined | 1 | PTM
| TM1 | 2010-08-23 00:56 | Equipment | Recloser/breaker faulted/mechanical | 0 | PTM
| TM1 | 2010-08-26 12:08 | Undetermined | Undetermined | 0 | PTM
| TM1 | 2011-11-21 18:26 | Undetermined | Undetermined | 0 | PTM
| TM1 | 2013-03-04 20:13 | Equipment | Cutout failure | 0 | PTM
| TM1 | 2013-03-23 11:16 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PTM
| TM1 | 2013-07-22 08:34 | Undetermined | Undetermined | 0 | PTM
| TM1 | 2013-08-10 11:00 | Undetermined | Undetermined | 0 | PTM
| TM1 | 2014-05-25 16:23 | Undetermined | Undetermined | 0 | PTM

## ExtCauseExcl
Circuit | Occurrence | Cause Category | Cause Description | Control Date | Station Code | FireWeather | Reclose
1001 | 2005-01-10 05:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0
1001 | 2005-02-21 07:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0 | 2005-01-01 | 38353 | Frequency | Rate
1001 | 2006-01-13 08:32 | Undetermined | Undetermined | 0 | RSF | 0 | 0 | 2006-01-01 | 2006-01-01 | 218 | 210.439
1001 | 2006-10-14 11:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0 | 2007-01-01 | 2007-01-01 | 222
1001 | 2007-08-16 15:28 | Undetermined | Undetermined | 0 | RSF | 0 | 0 | 2008-01-01 | 2008-01-01 | 244
1001 | 2009-08-15 13:07 | Equipment | Conductor failure/wire down | 0 | RSF | 0 | 0 | 2009-01-01 | 2009-01-01 | 216
1001 | 2010-05-12 19:37 | Undetermined | Undetermined | 0 | RSF | 0 | 0 | 2010-01-01 | 2010-01-01 | 201
1001 | 2010-12-23 23:40 | Equipment | Conductor failure/wire down | 0 | RSF | 0 | 0 | 2011-01-01 | 2011-01-01 | 270
1001 | 2012-02-27 23:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0 | 2012-01-01 | 2012-01-01 | 198
1001 | 2014-05-19 12:48 | Undetermined | Undetermined | 0 | RSF | 0 | 0 | 2013-01-01 | 2013-01-01 | 231
1001 | 2014-11-07 01:23 | Equipment | Pole broke/rotted/on fire | 0 | RSF | 0 | 0 | 2014-01-01 | 2014-01-01 | 180
1001 | 2015-01-16 18:50 | Undetermined | Undetermined | 0 | RSF | 0 | 0 | 2015-01-01 | 2015-01-01 | 218
1021 | 2010-09-30 13:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 0 | 2016-01-01 | 2016-01-01 | 39
1021 | 2011-02-02 01:13 | Weather | Wind - wires slap/pole down | 0 | HID | 1 | 0 |  | More | 0
1021 | 2012-11-06 12:44 | Equipment | Cutout failure | 0 | HID | 0 | 0 | 2015-03-15 | Total | 2237
1021 | 2012-12-13 03:48 | Foreign Object | Flashover/vegetation | 0 | HID | 0 | 0 |  | No Recl. | 2157
1021 | 2013-02-13 11:30 | Equipment | Pole broke/rotted/on fire | 0 | HID | 0 | 0
1021 | 2013-10-06 12:59 | Undetermined | Undetermined | 0 | HID | 0 | 0
1021 | 2014-07-18 21:32 | Undetermined | Undetermined | 0 | HID | 0 | 0
1021 | 2014-10-01 13:01 | Undetermined | Undetermined | 0 | HID | 0 | 0
1030 | 2005-01-22 08:42 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2005-05-20 04:06 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2005-06-04 09:24 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2006-08-12 14:24 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2006-10-15 15:31 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2007-03-13 10:40 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2007-09-30 05:50 | Equipment | Conductor failure/wire down | 0 | HHC | 0 | 0
1030 | 2007-10-16 14:06 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2007-10-22 00:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC | 1 | 0
1030 | 2007-10-22 00:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC | 1 | 1
1030 | 2007-10-22 02:06 | Weather | Wind - wires slap/pole down | 0 | HHC | 1 | 0
1030 | 2008-01-03 11:46 | Equipment | Crossarm failure | 0 | HHC | 0 | 0
1030 | 2008-11-25 12:20 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2009-01-26 23:22 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2009-04-16 12:33 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2010-01-18 16:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC | 0 | 0
1030 | 2011-01-23 05:20 | Undetermined | Undetermined | 0 | HHC | 1 | 0
1030 | 2011-02-09 09:22 | Equipment | Conductor contact/wire slap | 0 | HHC | 0 | 0
1030 | 2011-02-14 22:50 | Equipment | Conductor failure/wire down | 0 | HHC | 0 | 0
1030 | 2011-09-03 18:41 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2011-09-27 14:15 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2011-11-02 08:09 | Weather | Wind - wires slap/pole down | 0 | HHC | 0 | 0
1030 | 2011-11-09 23:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC | 0 | 0
1030 | 2012-09-10 15:04 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2012-12-27 22:53 | Undetermined | Undetermined | 0 | HHC | 0 | 0
1030 | 2013-03-08 05:54 | Equipment | Insulator/pin failure/wire floating | 0 | HHC | 0 | 0
1030 | 2013-05-06 05:47 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HHC | 0 | 0
1030 | 2014-03-09 12:44 | Equipment | Insulator/pin failure/wire floating | 0 | HHC | 1 | 0
1030 | 2014-05-14 10:26 | Equipment | Pole broke/rotted/on fire | 0 | HHC | 0 | 0
1094 | 2009-06-03 09:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OLV | 0 | 0
1094 | 2009-07-20 14:20 | Equipment | Cutout failure | 0 | OLV | 0 | 0
1094 | 2011-02-20 01:46 | Weather | Wind - wires slap/pole down | 0 | OLV | 0 | 0
1100 | 2005-09-20 02:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB | 0 | 0
1100 | 2011-11-12 17:25 | Undetermined | Undetermined | 0 | WRB | 0 | 0
1100 | 2011-11-18 13:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WRB | 0 | 0
1100 | 2011-12-06 | Undetermined | Undetermined | 0 | WRB | 0 | 0
1100 | 2011-12-06 09:38 | Weather | Wind - wires slap/pole down | 0 | WRB | 0 | 0
1101 | 2007-10-22 01:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB | 1 | 0
1101 | 2007-10-22 02:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB | 1 | 0
1166 | 2005-01-18 20:00 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2005-06-30 06:09 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2006-08-07 07:29 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2006-08-11 07:33 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2006-12-10 01:23 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD | 0 | 0
1166 | 2008-02-03 18:15 | Weather | Wind - wires slap/pole down | 0 | LLD | 0 | 0
1166 | 2009-05-13 10:03 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2010-01-22 07:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLD | 0 | 0
1166 | 2010-11-20 13:08 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2011-01-30 15:36 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1166 | 2011-04-30 23:13 | Equipment | Pole broke/rotted/on fire | 0 | LLD | 0 | 0
1166 | 2012-02-15 17:57 | Foreign Object | Flashover/vegetation | 0 | LLD | 0 | 0
1166 | 2012-07-21 16:36 | Equipment | Crossarm failure | 0 | LLD | 0 | 0
1166 | 2012-10-26 06:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLD | 0 | 0
1166 | 2014-11-01 04:56 | Undetermined | Undetermined | 0 | LLD | 0 | 0
1215 | 2006-03-11 07:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD | 0 | 0
1215 | 2006-03-12 07:14 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2007-01-06 03:45 | Weather | Wind - wires slap/pole down | 0 | CWD | 1 | 0
1215 | 2007-01-12 02:39 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2007-02-28 23:42 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2007-10-22 09:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD | 1 | 0
1215 | 2007-12-22 07:43 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CWD | 0 | 0
1215 | 2008-01-05 07:41 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2008-01-13 02:56 | Equipment | Crossarm failure | 0 | CWD | 0 | 0
1215 | 2008-03-16 06:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD | 0 | 0
1215 | 2008-12-17 10:08 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2010-09-29 15:09 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2011-02-20 01:39 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2011-02-20 05:55 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2011-07-05 17:41 | Undetermined | Undetermined | 1 | CWD | 0 | 0
1215 | 2011-08-05 23:20 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2011-11-11 13:08 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2012-01-25 10:15 | Equipment | Pole broke/rotted/on fire | 0 | CWD | 0 | 0
1215 | 2012-03-17 21:17 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2012-03-18 14:19 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2012-03-18 22:41 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2012-03-24 21:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD | 0 | 0
1215 | 2012-04-14 04:11 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2012-08-01 09:44 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2012-11-08 09:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CWD | 0 | 0
1215 | 2013-09-05 15:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD | 0 | 0
1215 | 2013-11-27 19:51 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2013-12-07 08:02 | Weather | Wind - wires slap/pole down | 0 | CWD | 0 | 0
1215 | 2014-04-30 07:45 | Weather | Wind - wires slap/pole down | 0 | CWD | 1 | 0
1215 | 2014-05-01 06:55 | Equipment | Conductor contact/wire slap | 0 | CWD | 1 | 0
1215 | 2014-11-18 06:42 | Undetermined | Undetermined | 0 | CWD | 0 | 0
1215 | 2015-02-05 05:49 | Equipment | Conductor failure/wire down | 0 | CWD | 0 | 0
1233 | 2009-04-13 17:10 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBH | 0 | 0
1233 | 2010-01-21 13:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBH | 0 | 0
1233 | 2013-01-30 17:00 | Undetermined | Undetermined | 0 | RBH | 0 | 0
1233 | 2013-06-17 11:03 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBH | 0 | 0
1233 | 2013-10-09 23:20 | Undetermined | Undetermined | 0 | RBH | 0 | 0
1233 | 2014-02-28 15:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBH | 0 | 0
1233 | 2014-03-02 11:43 | Undetermined | Undetermined | 0 | RBH | 0 | 0
1233 | 2014-12-18 19:18 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBH | 0 | 0
1234 | 2012-12-30 13:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
1234 | 2013-05-02 13:14 | Weather | Wind - wires slap/pole down | 0 | FBK | 0 | 0
1234 | 2013-11-01 11:33 | Undetermined | Undetermined | 0 | FBK | 0 | 0
1234 | 2014-03-10 08:14 | Undetermined | Undetermined | 0 | FBK | 0 | 0
1234 | 2015-01-20 17:15 | Equipment | Cutout failure | 0 | FBK | 0 | 0
1250 | 2005-01-20 11:02 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1250 | 2005-01-20 11:12 | Equipment | Conductor failure/wire down | 0 | RSF | 0 | 1
1250 | 2005-05-01 07:31 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1250 | 2005-09-06 16:46 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RSF | 0 | 0
1250 | 2006-04-10 01:30 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1250 | 2008-03-27 11:21 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1250 | 2008-03-27 18:31 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1250 | 2008-09-14 11:56 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RSF | 0 | 0
1250 | 2009-06-03 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0
1250 | 2010-01-21 23:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0
1250 | 2012-08-07 09:54 | Equipment | Crossarm failure | 0 | RSF | 0 | 0
1250 | 2012-12-31 18:08 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1250 | 2013-05-31 16:41 | Undetermined | Undetermined | 0 | RSF | 0 | 0
1458 | 2006-07-21 18:35 | Undetermined | Undetermined | 0 | ANE | 0 | 0
1458 | 2007-03-21 01:10 | Undetermined | Undetermined | 0 | ANE | 0 | 0
1458 | 2007-10-22 11:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0
1458 | 2007-10-23 08:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0
1458 | 2008-02-14 14:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
1458 | 2009-01-11 02:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0
1458 | 2009-11-28 18:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
1458 | 2010-09-30 17:41 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
1458 | 2011-05-08 23:32 | Undetermined | Undetermined | 0 | ANE | 0 | 0
1458 | 2011-11-16 05:57 | Equipment | Cutout failure | 0 | ANE | 0 | 0
1458 | 2012-06-02 16:16 | Undetermined | Undetermined | 0 | ANE | 0 | 0
1458 | 2013-02-16 09:23 | Undetermined | Undetermined | 0 | ANE | 0 | 0
157 | 2005-03-31 13:21 | Weather | Circuit Flashover/fog/foreign object | 0 | BAJC1 | 1 | 0
157 | 2005-07-06 07:52 | Undetermined | Undetermined | 1 | BAJC1 | 0 | 0
157 | 2005-11-14 15:58 | Undetermined | Undetermined | 0 | BAJC1 | 1 | 0
157 | 2005-12-23 07:04 | Equipment | Cutout failure | 0 | BAJC1 | 0 | 0
157 | 2006-02-26 11:04 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2006-07-19 11:44 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2006-08-23 08:25 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BAJC1 | 0 | 0
157 | 2006-09-03 12:53 | Weather | Wind - wires slap/pole down | 0 | BAJC1 | 0 | 0
157 | 2006-10-13 05:00 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2007-03-03 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 1 | 0
157 | 2007-07-10 14:07 | Equipment | Conductor failure/wire down | 1 | BAJC1 | 0 | 0
157 | 2007-10-21 09:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 1 | 0
157 | 2008-01-27 04:20 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2008-02-14 19:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 0 | 0
157 | 2008-03-30 08:21 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2008-04-08 04:24 | Equipment | Crossarm failure | 0 | BAJC1 | 0 | 0
157 | 2008-05-06 05:44 | Equipment | Insulator/pin failure/wire floating | 0 | BAJC1 | 0 | 0
157 | 2008-11-08 10:55 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2009-09-24 23:23 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2009-10-18 14:19 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2009-11-13 06:51 | Equipment | Pole broke/rotted/on fire | 0 | BAJC1 | 0 | 0
157 | 2009-12-01 14:55 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2009-12-07 16:25 | Weather | Wind - wires slap/pole down | 0 | BAJC1 | 0 | 0
157 | 2009-12-07 17:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 0 | 0
157 | 2009-12-23 03:44 | Weather | Wind - wires slap/pole down | 0 | BAJC1 | 0 | 0
157 | 2010-07-03 11:38 | Undetermined | Undetermined | 1 | BAJC1 | 0 | 0
157 | 2010-08-22 05:41 | Equipment | Conductor failure/wire down | 0 | BAJC1 | 0 | 0
157 | 2010-09-30 14:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 0 | 0
157 | 2010-10-20 01:08 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2011-05-08 22:48 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2011-05-15 12:02 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2011-05-16 09:41 | Equipment | Conductor failure/wire down | 0 | BAJC1 | 0 | 0
157 | 2011-06-17 09:50 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2011-11-13 09:30 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2012-05-12 09:04 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2012-05-16 23:03 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2012-05-30 14:45 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2012-07-09 18:22 | Undetermined | Undetermined | 1 | BAJC1 | 0 | 0
157 | 2013-09-27 06:25 | Undetermined | Undetermined | 0 | BAJC1 | 0 | 0
157 | 2014-04-30 06:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 1 | 0
157 | 2014-05-13 07:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 0 | 0
157 | 2014-05-13 09:27 | Weather | Wind - wires slap/pole down | 0 | BAJC1 | 0 | 0
170 | 2005-01-11 14:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
170 | 2005-04-09 01:33 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 0
170 | 2005-04-10 07:16 | Equipment | Conductor failure/wire down | 0 | BRG | 0 | 0
170 | 2005-12-03 13:18 | Equipment | Cutout failure | 0 | BRG | 0 | 0
170 | 2006-04-06 06:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
170 | 2006-05-14 05:42 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2007-01-05 11:43 | Equipment | Conductor failure/wire down | 0 | BRG | 1 | 0
170 | 2007-01-27 11:35 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2007-03-10 11:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
170 | 2007-12-02 02:16 | Equipment | Conductor failure/wire down | 0 | BRG | 0 | 0
170 | 2007-12-16 03:34 | Equipment | Conductor failure/wire down | 0 | BRG | 0 | 0
170 | 2008-01-28 12:51 | Equipment | Cutout failure | 0 | BRG | 0 | 0
170 | 2008-02-02 14:33 | Equipment | Conductor failure/wire down | 0 | BRG | 0 | 0
170 | 2008-05-24 09:30 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2008-10-04 19:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
170 | 2008-11-28 12:06 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2008-12-18 11:44 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2008-12-20 12:14 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2008-12-22 14:59 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2009-03-22 10:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
170 | 2009-03-25 18:42 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2009-05-03 16:48 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2009-11-05 08:11 | Equipment | Pole broke/rotted/on fire | 0 | BRG | 0 | 0
170 | 2009-12-07 14:44 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 0
170 | 2010-01-22 07:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
170 | 2010-07-16 12:59 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2010-07-16 16:07 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2011-09-05 13:58 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2011-09-05 22:37 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2012-01-21 14:27 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 0
170 | 2012-12-15 20:28 | Equipment | Cutout failure | 0 | BRG | 0 | 0
170 | 2014-03-01 02:00 | Undetermined | Undetermined | 0 | BRG | 0 | 0
170 | 2015-01-01 21:30 | Equipment | Conductor failure/wire down | 0 | BRG | 0 | 0
172 | 2006-05-10 23:12 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2006-05-23 01:43 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2006-06-28 01:54 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2007-05-30 05:30 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2008-02-03 12:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2008-02-03 17:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2008-05-21 10:13 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2008-11-27 06:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BRG | 0 | 0
172 | 2008-12-05 16:25 | Undetermined | Undetermined | 0 | BRG | 1 | 0
172 | 2009-03-22 11:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2009-03-22 16:26 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2009-04-14 21:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2009-12-07 22:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2009-12-08 05:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2010-04-11 21:46 | Equipment | Crossarm failure | 0 | BRG | 0 | 0
172 | 2010-04-28 21:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2010-09-06 05:53 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2010-09-30 08:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2010-10-20 04:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2011-03-07 08:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2011-05-23 11:57 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2011-07-03 16:04 | Undetermined | Undetermined | 1 | BRG | 0 | 0
172 | 2011-12-13 13:30 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2012-01-21 12:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2012-01-21 13:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2012-01-21 14:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 0
172 | 2012-01-21 14:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 1
172 | 2012-01-21 14:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 1
172 | 2012-01-21 14:21 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 1
172 | 2012-03-06 20:48 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2012-09-09 20:29 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 0
172 | 2013-02-21 15:35 | Undetermined | Undetermined | 0 | BRG | 0 | 0
172 | 2013-04-08 08:14 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 0
172 | 2013-04-08 09:00 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 0
172 | 2013-04-08 09:05 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 1
172 | 2013-12-07 23:38 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BRG | 0 | 0
172 | 2014-03-30 17:54 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BRG | 0 | 0
172 | 2014-03-30 19:33 | Undetermined | Undetermined | 0 | BRG | 0 | 0
175 | 2005-01-04 13:00 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
175 | 2005-03-19 14:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2005-09-14 10:13 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH | 0 | 0
175 | 2005-09-14 18:23 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH | 0 | 0
175 | 2007-11-26 10:30 | Equipment | Conductor contact/wire slap | 0 | ARH | 0 | 0
175 | 2007-11-28 08:02 | Equipment | Conductor contact/wire slap | 0 | ARH | 0 | 0
175 | 2007-11-28 08:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2007-12-25 09:08 | Equipment | Conductor contact/wire slap | 0 | ARH | 0 | 0
175 | 2007-12-31 15:39 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
175 | 2007-12-31 21:26 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
175 | 2008-01-01 07:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 1 | 0
175 | 2008-01-03 11:30 | Equipment | Conductor contact/wire slap | 0 | ARH | 0 | 0
175 | 2008-05-16 08:51 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2008-05-29 20:41 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2008-11-15 11:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2008-12-17 09:51 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
175 | 2008-12-17 11:10 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
175 | 2008-12-17 11:15 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1
175 | 2008-12-17 11:20 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1
175 | 2008-12-17 11:25 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1
175 | 2008-12-17 11:30 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1
175 | 2008-12-17 11:37 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1
175 | 2010-01-19 14:31 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
175 | 2010-01-19 18:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2010-03-02 05:47 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2010-03-25 11:59 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2010-09-01 10:32 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2010-09-30 13:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2010-09-30 17:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2011-02-06 06:28 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2012-01-11 06:51 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2012-05-03 14:57 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2012-05-29 09:44 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH | 0 | 0
175 | 2012-07-16 12:26 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2013-01-12 16:24 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2013-05-03 05:43 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2014-04-06 08:06 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2014-11-29 05:19 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2014-11-29 23:13 | Undetermined | Undetermined | 0 | ARH | 0 | 0
175 | 2014-12-12 08:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
175 | 2014-12-26 05:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH | 0 | 0
176 | 2005-01-04 13:24 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
176 | 2005-01-04 21:15 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
176 | 2005-01-07 16:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2005-01-07 18:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2005-01-07 23:51 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
176 | 2005-01-10 10:51 | Equipment | Connector/jumper/splice/elbow/rack | 0 | ARH | 0 | 0
176 | 2005-08-25 15:03 | Equipment | Crossarm failure | 0 | ARH | 0 | 0
176 | 2005-09-20 10:53 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
176 | 2005-12-06 02:47 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2006-07-15 16:16 | Weather | Circ. Flashover/storm/high winds/undet. | 1 | ARH | 0 | 0
176 | 2006-07-30 04:39 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2006-09-04 17:33 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2007-08-03 17:20 | Equipment | Pole broke/rotted/on fire | 0 | ARH | 0 | 0
176 | 2007-10-24 23:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2007-10-25 13:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2007-11-30 18:26 | Equipment | Conductor failure/wire down | 0 | ARH | 0 | 0
176 | 2007-12-02 11:06 | Equipment | Conductor failure/wire down | 0 | ARH | 0 | 0
176 | 2007-12-17 16:33 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2008-01-07 04:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2008-03-25 09:00 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2008-10-16 12:40 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2009-03-31 09:00 | Equipment | Cutout failure | 0 | ARH | 0 | 0
176 | 2010-01-19 14:26 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 0
176 | 2010-01-20 03:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2010-02-08 04:47 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2010-09-30 13:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 0
176 | 2010-09-30 13:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 1
176 | 2010-09-30 13:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 1
176 | 2011-08-21 08:39 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2011-12-21 09:30 | Equipment | Pole broke/rotted/on fire | 0 | ARH | 0 | 0
176 | 2012-08-22 11:02 | Equipment | Crossarm failure | 0 | ARH | 0 | 0
176 | 2013-10-11 12:02 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2014-02-19 17:55 | Undetermined | Undetermined | 0 | ARH | 0 | 0
176 | 2014-12-13 03:15 | Equipment | Conductor failure/wire down | 0 | ARH | 0 | 0
181 | 2005-01-04 07:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ESC | 0 | 0
181 | 2007-05-28 07:31 | Undetermined | Undetermined | 0 | ESC | 0 | 0
181 | 2011-09-30 23:24 | Undetermined | Undetermined | 0 | ESC | 0 | 0
204 | 2005-01-11 03:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP | 0 | 0
204 | 2005-05-12 08:15 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2005-06-13 13:52 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2005-06-24 19:54 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2005-11-13 08:27 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2005-11-14 08:54 | Undetermined | Undetermined | 0 | CAP | 1 | 0
204 | 2005-12-02 22:47 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2005-12-04 08:55 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2006-01-10 14:48 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2006-07-27 10:49 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2007-01-31 11:33 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2007-04-23 09:20 | Equipment | Cutout failure | 0 | CAP | 0 | 0
204 | 2009-06-03 08:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP | 0 | 0
204 | 2009-09-09 10:38 | Undetermined | Undetermined | 0 | CAP | 0 | 0
204 | 2010-08-22 00:12 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CAP | 0 | 0
204 | 2010-10-19 12:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP | 0 | 0
204 | 2013-10-24 05:57 | Undetermined | Undetermined | 0 | CAP | 0 | 0
206 | 2005-01-11 03:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 0 | 0
206 | 2005-03-28 08:40 | Equipment | Crossarm failure | 0 | CBD | 0 | 0
206 | 2006-01-02 00:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 0 | 0
206 | 2006-01-02 10:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 0 | 0
206 | 2006-01-02 12:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 0 | 0
206 | 2006-01-02 14:00 | Weather | Wind - wires slap/pole down | 0 | CBD | 0 | 0
206 | 2006-08-24 17:51 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2007-07-26 14:03 | Equipment | Cutout failure | 0 | CBD | 0 | 0
206 | 2007-10-22 04:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 1 | 0
206 | 2008-05-24 17:41 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2008-12-09 14:40 | Equipment | Conductor failure/wire down | 0 | CBD | 1 | 0
206 | 2009-11-22 22:04 | Equipment | Cutout failure | 0 | CBD | 0 | 0
206 | 2009-12-07 17:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 0 | 0
206 | 2010-01-23 12:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 0 | 0
206 | 2010-11-23 03:21 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2010-11-24 06:07 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2011-06-22 13:01 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2011-10-24 12:52 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2012-11-02 16:45 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2012-12-25 10:16 | Undetermined | Undetermined | 0 | CBD | 0 | 0
206 | 2012-12-25 11:11 | Equipment | Conductor failure/wire down | 0 | CBD | 0 | 0
206 | 2013-10-11 10:05 | Undetermined | Undetermined | 0 | CBD | 0 | 0
210 | 2005-05-12 13:52 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2005-08-07 12:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY | 0 | 0
210 | 2005-08-09 08:03 | Weather | Wind - wires slap/pole down | 0 | COY | 0 | 0
210 | 2005-09-19 23:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY | 0 | 0
210 | 2006-02-25 07:31 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2007-06-23 06:24 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2007-07-20 07:21 | Equipment | Cutout failure | 0 | COY | 0 | 0
210 | 2007-10-24 17:47 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2008-11-04 10:55 | Equipment | Cutout failure | 0 | COY | 0 | 0
210 | 2009-01-10 10:10 | Undetermined | Undetermined | 0 | COY | 1 | 0
210 | 2010-06-27 13:30 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2010-08-26 13:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY | 0 | 0
210 | 2010-09-30 07:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY | 0 | 0
210 | 2010-10-19 19:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY | 0 | 0
210 | 2010-11-27 08:17 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2011-04-13 16:30 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2011-06-14 09:20 | Equipment | Conductor failure/wire down | 0 | COY | 0 | 0
210 | 2011-08-04 06:17 | Equipment | Conductor failure/wire down | 0 | COY | 0 | 0
210 | 2012-06-10 19:40 | Equipment | Crossarm failure | 0 | COY | 0 | 0
210 | 2012-12-18 15:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | COY | 0 | 0
210 | 2013-02-11 21:08 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2013-09-02 14:41 | Undetermined | Undetermined | 0 | COY | 0 | 0
210 | 2013-12-27 00:01 | Undetermined | Undetermined | 0 | COY | 0 | 0
211 | 2005-04-22 12:18 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2005-05-23 11:27 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2005-07-30 16:00 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2005-10-28 19:13 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2005-11-18 18:05 | Undetermined | Undetermined | 0 | EWN | 1 | 0
211 | 2005-11-26 17:06 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2005-12-31 06:47 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2006-06-20 16:05 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2006-07-15 17:03 | Weather | Circ. Flashover/storm/high winds/undet. | 1 | EWN | 0 | 0
211 | 2006-10-04 15:06 | Equipment | Crossarm failure | 0 | EWN | 0 | 0
211 | 2006-12-28 08:33 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2007-01-12 08:15 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2007-04-21 06:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN | 0 | 0
211 | 2007-06-08 08:51 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2008-02-04 01:02 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN | 0 | 0
211 | 2008-09-11 17:04 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2008-10-20 01:15 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2008-10-24 10:40 | Equipment | Crossarm failure | 0 | EWN | 0 | 0
211 | 2009-02-12 23:30 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2009-09-25 04:23 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2010-02-24 19:19 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2010-03-15 11:51 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2010-11-16 07:57 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2011-02-20 05:13 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2011-05-02 12:30 | Weather | Wind - wires slap/pole down | 0 | EWN | 0 | 0
211 | 2011-05-29 11:47 | Equipment | Crossarm failure | 0 | EWN | 0 | 0
211 | 2011-09-13 10:38 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2012-03-18 01:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN | 0 | 0
211 | 2012-03-18 09:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN | 0 | 0
211 | 2012-03-18 10:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN | 0 | 0
211 | 2012-03-18 10:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | EWN | 0 | 0
211 | 2012-03-18 12:02 | Weather | Wind - wires slap/pole down | 0 | EWN | 0 | 0
211 | 2012-04-14 05:49 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2012-04-14 06:43 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2012-04-14 06:53 | Undetermined | Undetermined | 0 | EWN | 0 | 1
211 | 2012-04-14 07:03 | Undetermined | Undetermined | 0 | EWN | 0 | 1
211 | 2012-04-14 07:10 | Undetermined | Undetermined | 0 | EWN | 0 | 1
211 | 2013-01-14 05:41 | Undetermined | Undetermined | 0 | EWN | 0 | 0
211 | 2013-03-21 07:33 | Undetermined | Undetermined | 0 | EWN | 0 | 0
212 | 2005-03-08 17:00 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2005-03-28 20:47 | Equipment | Cutout failure | 0 | MGY | 0 | 0
212 | 2005-12-22 06:30 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2006-01-01 06:37 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2006-02-10 11:16 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2006-03-21 08:10 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2006-05-06 06:45 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2006-06-06 17:22 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2007-02-18 16:55 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2007-08-01 15:19 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2007-08-25 17:38 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2007-10-13 09:06 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2007-11-30 05:42 | Equipment | Crossarm failure | 0 | MGY | 0 | 0
212 | 2008-01-05 07:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2008-01-05 13:31 | Equipment | Pole broke/rotted/on fire | 0 | MGY | 0 | 0
212 | 2008-04-07 06:14 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-06-07 09:30 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-06-17 12:56 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-06-20 12:08 | Equipment | Conductor failure/wire down | 0 | MGY | 0 | 0
212 | 2008-07-15 08:46 | Undetermined | Undetermined | 1 | MGY | 0 | 0
212 | 2008-07-16 03:47 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-07-20 06:05 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-07-25 11:27 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-09-01 11:16 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-09-11 17:34 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2008-09-14 14:33 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2009-05-07 16:39 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2009-05-19 15:10 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGY | 0 | 0
212 | 2009-11-18 08:41 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2009-12-07 20:14 | Weather | Wind - wires slap/pole down | 0 | MGY | 0 | 0
212 | 2010-01-31 08:04 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-03-02 03:21 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-04-05 08:59 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-05-16 15:45 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-08-26 11:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2010-09-10 18:50 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-10-24 22:52 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-11-15 12:52 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-12-08 06:13 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-12-14 09:33 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-12-17 16:11 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2010-12-20 13:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2011-01-15 07:25 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2011-01-20 13:02 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2011-01-31 06:26 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2011-02-15 06:11 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2011-02-26 08:24 | Weather | Wind - wires slap/pole down | 0 | MGY | 0 | 0
212 | 2011-03-11 05:40 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2011-07-30 15:39 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2011-08-28 14:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2011-12-16 13:44 | Equipment | Conductor failure/wire down | 0 | MGY | 0 | 0
212 | 2011-12-18 06:14 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2012-02-14 06:18 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2012-02-27 20:37 | Weather | Wind - wires slap/pole down | 0 | MGY | 0 | 0
212 | 2012-04-10 03:28 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2012-08-07 12:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2012-08-22 13:00 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2012-08-30 13:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2012-12-24 06:56 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2012-12-25 06:34 | Equipment | Conductor failure/wire down | 0 | MGY | 0 | 0
212 | 2013-02-05 07:53 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2013-02-20 05:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2013-03-20 19:25 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2013-05-06 07:11 | Equipment | Crossarm failure | 0 | MGY | 0 | 0
212 | 2013-05-06 13:36 | Equipment | Crossarm failure | 0 | MGY | 0 | 0
212 | 2013-05-10 05:49 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2013-05-16 03:18 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2013-05-16 11:29 | Equipment | Crossarm failure | 0 | MGY | 0 | 0
212 | 2013-07-22 14:16 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2013-09-02 15:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGY | 0 | 0
212 | 2013-09-28 17:12 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2014-02-03 21:36 | Equipment | Conductor contact/wire slap | 0 | MGY | 0 | 0
212 | 2014-03-30 10:17 | Undetermined | Undetermined | 0 | MGY | 0 | 0
212 | 2015-01-26 13:56 | Weather | Wind - wires slap/pole down | 0 | MGY | 0 | 0
214 | 2005-01-03 17:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2005-02-02 09:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2005-04-20 06:41 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2005-06-20 10:09 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2005-08-20 20:36 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2005-12-29 12:50 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 0
214 | 2006-07-28 10:29 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2006-10-05 20:12 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2006-10-06 15:39 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2007-01-24 12:34 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2007-03-04 08:50 | Undetermined | Undetermined | 0 | RIN | 1 | 0
214 | 2007-06-06 10:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2007-08-15 20:04 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2007-09-22 08:42 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2007-09-29 20:20 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2007-11-30 05:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2008-12-16 13:38 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2009-02-09 06:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2009-06-07 19:18 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2009-12-07 11:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2010-01-21 08:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2010-03-24 17:30 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2010-06-12 02:35 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2010-08-22 19:19 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 0
214 | 2010-09-27 13:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
214 | 2011-01-31 10:40 | Equipment | Conductor contact/wire slap | 0 | RIN | 0 | 0
214 | 2012-02-15 16:53 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2013-04-19 09:44 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2014-04-28 13:39 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 0
214 | 2014-04-30 09:14 | Undetermined | Undetermined | 0 | RIN | 1 | 0
214 | 2014-08-03 16:02 | Undetermined | Undetermined | 0 | RIN | 0 | 0
214 | 2014-08-04 09:23 | Undetermined | Undetermined | 0 | RIN | 0 | 0
215 | 2005-02-02 13:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
215 | 2005-02-03 12:03 | Weather | Wind - wires slap/pole down | 0 | RIN | 0 | 0
215 | 2005-09-20 08:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
215 | 2006-01-02 10:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
215 | 2006-04-05 01:16 | Weather | Wind - wires slap/pole down | 0 | RIN | 0 | 0
215 | 2007-10-29 10:48 | Undetermined | Undetermined | 0 | RIN | 0 | 0
215 | 2008-05-22 19:40 | Undetermined | Undetermined | 0 | RIN | 0 | 0
215 | 2009-02-20 20:09 | Equipment | Pole broke/rotted/on fire | 0 | RIN | 0 | 0
215 | 2010-12-20 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
215 | 2010-12-20 18:26 | Weather | Wind - wires slap/pole down | 0 | RIN | 0 | 0
215 | 2013-02-23 13:27 | Undetermined | Undetermined | 0 | RIN | 0 | 0
215 | 2013-06-03 06:10 | Undetermined | Undetermined | 0 | RIN | 0 | 0
215 | 2014-02-28 06:48 | Weather | Wind - wires slap/pole down | 0 | RIN | 0 | 0
215 | 2014-02-28 08:51 | Weather | Wind - wires slap/pole down | 0 | RIN | 0 | 0
215 | 2014-02-28 15:07 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 0
215 | 2014-03-18 15:00 | Equipment | Insulator/pin failure/wire floating | 0 | RIN | 0 | 0
216 | 2005-04-01 10:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 1 | 0
216 | 2005-11-02 14:16 | Undetermined | Undetermined | 0 | RIN | 0 | 0
216 | 2005-12-11 13:49 | Undetermined | Undetermined | 0 | RIN | 0 | 0
216 | 2006-01-02 08:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 0
216 | 2006-01-02 10:48 | Weather | Wind - wires slap/pole down | 0 | RIN | 0 | 0
216 | 2006-02-05 11:04 | Undetermined | Undetermined | 0 | RIN | 1 | 0
216 | 2006-02-08 12:21 | Undetermined | Undetermined | 0 | RIN | 1 | 0
216 | 2007-03-04 09:31 | Undetermined | Undetermined | 0 | RIN | 1 | 0
216 | 2008-05-02 06:51 | Equipment | Insulator/pin failure/wire floating | 0 | RIN | 0 | 0
216 | 2009-01-19 09:08 | Equipment | Cutout failure | 0 | RIN | 0 | 0
217 | 2005-05-03 20:04 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2005-05-03 20:04 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-01-23 19:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 1 | 0
217 | 2006-01-23 19:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 1 | 1
217 | 2006-01-24 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2006-01-24 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2006-05-05 17:55 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2006-05-05 17:55 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-06-04 04:14 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2006-06-04 04:14 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-09-22 13:45 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2006-09-22 13:45 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-11-26 16:34 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2006-11-26 16:34 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-12-09 21:48 | Equipment | Cutout failure | 0 | PAU | 0 | 0
217 | 2006-12-09 21:48 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2007-07-05 01:46 | Equipment | Connector/jumper/splice/elbow/rack | 1 | PAU | 0 | 0
217 | 2007-07-05 01:46 | Equipment | Connector/jumper/splice/elbow/rack | 1 | RIN | 0 | 1
217 | 2007-09-11 10:21 | Equipment | Cutout failure | 0 | PAU | 0 | 0
217 | 2007-09-11 10:21 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2007-09-21 03:23 | Equipment | Conductor failure/wire down | 0 | PAU | 0 | 0
217 | 2007-09-21 03:23 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2007-09-29 18:34 | Equipment | Conductor contact/wire slap | 0 | PAU | 0 | 0
217 | 2007-09-29 18:34 | Equipment | Conductor contact/wire slap | 0 | RIN | 0 | 1
217 | 2008-11-18 19:28 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2008-11-18 19:28 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2008-12-25 11:12 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2008-12-25 11:12 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2009-02-04 14:07 | Equipment | Conductor failure/wire down | 0 | PAU | 0 | 0
217 | 2009-02-04 14:07 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2009-06-03 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2009-06-03 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2009-06-03 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 16:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 1
217 | 2009-06-03 16:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 16:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2009-06-03 16:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 19:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2009-06-03 19:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2010-09-04 14:07 | Equipment | Conductor failure/wire down | 0 | PAU | 0 | 0
217 | 2010-09-04 14:07 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2010-10-19 09:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2010-10-19 09:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2010-11-12 18:49 | Equipment | Cutout failure | 0 | PAU | 0 | 0
217 | 2010-11-12 18:49 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2011-01-23 06:44 | Equipment | Conductor failure/wire down | 0 | PAU | 1 | 0
217 | 2011-01-23 06:44 | Equipment | Conductor failure/wire down | 0 | RIN | 1 | 1
217 | 2011-01-26 19:31 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2011-01-26 19:31 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-03-02 10:50 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2011-03-02 10:50 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-05-29 05:06 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2011-05-29 05:06 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-06-11 10:30 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2011-06-11 10:30 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-07-03 03:25 | Undetermined | Undetermined | 1 | PAU | 0 | 0
217 | 2011-07-03 03:25 | Undetermined | Undetermined | 1 | RIN | 0 | 1
217 | 2012-03-20 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU | 0 | 0
217 | 2012-03-20 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 1
217 | 2012-04-19 07:26 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2012-04-19 07:26 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2013-01-08 12:01 | Equipment | Cutout failure | 0 | PAU | 0 | 0
217 | 2013-01-08 12:01 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2013-01-13 07:50 | Equipment | Conductor failure/wire down | 0 | PAU | 0 | 0
217 | 2013-01-13 07:50 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | PAU | 0 | 0
217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | RIN | 0 | 1
217 | 2013-12-27 14:35 | Equipment | Pole broke/rotted/on fire | 0 | PAU | 0 | 0
217 | 2013-12-27 14:35 | Equipment | Pole broke/rotted/on fire | 0 | RIN | 0 | 1
217 | 2014-02-28 18:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2014-02-28 18:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2014-04-29 16:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU | 0 | 0
217 | 2014-04-29 16:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 1
217 | 2014-04-30 08:11 | Undetermined | Undetermined | 0 | PAU | 1 | 0
217 | 2014-04-30 08:11 | Undetermined | Undetermined | 0 | RIN | 1 | 1
217 | 2014-04-30 11:21 | Equipment | Conductor failure/wire down | 0 | PAU | 1 | 0
217 | 2014-04-30 11:21 | Equipment | Conductor failure/wire down | 0 | RIN | 1 | 1
217 | 2014-05-14 12:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 0
217 | 2014-05-14 12:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2014-07-21 15:54 | Undetermined | Undetermined | 0 | PAU | 0 | 0
217 | 2014-07-21 15:54 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2014-12-20 12:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU | 0 | 0
217 | 2014-12-20 12:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 1
217 | 2015-01-24 04:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU | 1 | 0
217 | 2015-01-24 04:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 1 | 1
217 | 2015-01-24 07:04 | Equipment | Conductor contact/wire slap | 0 | PAU | 1 | 0
217 | 2015-01-24 07:04 | Equipment | Conductor contact/wire slap | 0 | RIN | 1 | 1
217 | 2015-01-24 09:26 | Undetermined | Undetermined | 0 | PAU | 1 | 0
217 | 2015-01-24 09:26 | Undetermined | Undetermined | 0 | RIN | 1 | 1
217 | 2015-01-24 14:23 | Equipment | Conductor contact/wire slap | 0 | PAU | 1 | 0
217 | 2015-01-24 14:23 | Equipment | Conductor contact/wire slap | 0 | RIN | 1 | 1
220 | 2005-01-10 16:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2005-03-02 10:54 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2005-07-04 08:01 | Undetermined | Undetermined | 1 | YSA | 0 | 0
220 | 2005-07-25 10:00 | Equipment | Pole broke/rotted/on fire | 0 | YSA | 0 | 0
220 | 2005-07-27 08:05 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2005-07-30 13:12 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2005-08-11 18:07 | Equipment | Cutout failure | 0 | YSA | 0 | 0
220 | 2005-09-20 08:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2005-09-20 10:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2005-11-10 09:36 | Equipment | Cutout failure | 0 | YSA | 0 | 0
220 | 2006-07-05 18:25 | Undetermined | Undetermined | 1 | YSA | 0 | 0
220 | 2006-07-18 13:56 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2006-11-30 06:19 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0
220 | 2007-03-30 01:00 | Equipment | Cutout failure | 0 | YSA | 0 | 0
220 | 2007-06-13 20:00 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA | 0 | 0
220 | 2007-07-02 12:05 | Undetermined | Undetermined | 1 | YSA | 0 | 0
220 | 2007-10-22 05:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0
220 | 2008-06-17 10:15 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2008-06-24 07:26 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2009-11-11 05:49 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2010-01-21 07:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2010-03-16 02:53 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2010-06-13 14:34 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2010-12-10 11:01 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2010-12-22 06:44 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
220 | 2011-01-25 13:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2011-02-02 06:12 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0
220 | 2011-02-11 08:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2012-07-09 08:00 | Undetermined | Undetermined | 1 | YSA | 0 | 0
220 | 2012-08-30 13:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2013-02-27 18:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2013-06-18 19:44 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2013-12-09 12:48 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2013-12-09 18:05 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2014-05-13 06:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
220 | 2014-07-26 12:07 | Undetermined | Undetermined | 0 | YSA | 0 | 0
220 | 2014-11-25 03:41 | Undetermined | Undetermined | 0 | YSA | 1 | 0
221 | 2005-04-01 11:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0
221 | 2005-04-09 00:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2005-04-19 01:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2005-06-03 01:41 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2005-08-07 00:14 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2005-09-19 23:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2005-10-12 06:47 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2005-12-03 09:10 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2005-12-24 16:09 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2006-01-18 22:43 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2006-01-19 04:38 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2006-02-15 16:08 | Equipment | Conductor failure/wire down | 0 | YSA | 0 | 0
221 | 2006-03-12 08:48 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2006-03-19 15:19 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2006-07-20 15:06 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2006-09-21 06:56 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2006-10-28 10:45 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2006-10-29 14:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2006-11-27 08:38 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2006-11-28 04:23 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2007-03-02 13:46 | Equipment | Cutout failure | 0 | YSA | 1 | 0
221 | 2007-03-15 12:23 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2007-10-05 05:07 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2007-10-05 07:40 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2007-12-01 06:36 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2007-12-01 07:39 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2008-01-05 04:52 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2008-02-03 12:59 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2008-02-03 13:35 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2008-02-03 17:55 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2008-02-03 18:51 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2008-05-28 06:45 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2008-08-16 09:07 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
221 | 2008-09-17 15:32 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2008-09-22 09:00 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2008-12-05 06:38 | Undetermined | Undetermined | 0 | YSA | 1 | 0
221 | 2008-12-18 14:22 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2008-12-19 05:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2009-02-09 07:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2009-02-13 14:19 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2009-02-16 08:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2009-03-22 12:43 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2009-04-02 13:01 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2009-05-20 16:22 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2009-09-28 06:18 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2009-11-13 04:58 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2009-12-07 19:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2009-12-07 20:27 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2009-12-07 22:15 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2009-12-08 01:59 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2009-12-22 08:38 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2009-12-22 13:20 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2010-01-18 15:58 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2010-01-18 19:23 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2010-03-09 08:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2010-05-21 15:57 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2010-06-18 18:52 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2010-06-18 19:24 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2010-07-20 10:41 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2010-08-14 14:31 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2010-08-26 18:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2010-09-30 04:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2010-09-30 11:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2010-11-16 19:30 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2011-01-06 06:22 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2011-05-21 19:04 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2011-05-31 19:27 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2011-07-09 05:51 | Undetermined | Undetermined | 1 | YSA | 0 | 0
221 | 2011-10-11 14:54 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2012-01-13 04:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2012-01-21 16:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2012-02-13 16:24 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2012-04-01 03:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2012-04-01 03:23 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
221 | 2012-04-13 17:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2012-08-07 12:00 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2012-10-12 17:13 | Undetermined | Undetermined | 0 | YSA | 0 | 0
221 | 2013-08-26 08:37 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2013-12-01 13:31 | Equipment | Pole broke/rotted/on fire | 0 | YSA | 0 | 0
221 | 2014-02-28 08:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
221 | 2014-04-07 10:13 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
221 | 2014-04-07 14:50 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
221 | 2014-04-13 08:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA | 0 | 0
221 | 2014-04-14 08:23 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
221 | 2014-06-27 19:47 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-01-09 06:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2005-02-12 14:01 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-02-25 15:41 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-03-05 17:26 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-03-13 06:29 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-04-01 05:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0
222 | 2005-05-06 00:43 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-05-16 08:18 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-06-08 23:54 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-07-18 19:28 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-08-04 07:59 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-11-04 15:12 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-11-27 06:06 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-12-01 16:23 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2005-12-30 16:47 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-04-21 14:07 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
222 | 2006-05-15 18:27 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-05-17 10:39 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-05-20 17:40 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-05-31 08:26 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-08-15 11:02 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-08-29 13:29 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-11-05 05:50 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-11-29 21:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2006-11-29 22:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2006-11-30 04:49 | Undetermined | Undetermined | 0 | YSA | 1 | 0
222 | 2006-11-30 10:41 | Undetermined | Undetermined | 0 | YSA | 1 | 0
222 | 2006-12-03 09:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA | 1 | 0
222 | 2006-12-03 11:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0
222 | 2006-12-07 06:49 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-12-26 06:22 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2006-12-28 06:26 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-01-04 23:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2007-01-06 02:15 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0
222 | 2007-01-07 06:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0
222 | 2007-01-07 08:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0
222 | 2007-01-15 06:20 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-01-15 07:08 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-02-12 06:18 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-03-09 09:23 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-03-13 15:04 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
222 | 2007-03-19 20:28 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-05-27 14:42 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-05-28 15:06 | Equipment | Conductor failure/wire down | 0 | YSA | 0 | 0
222 | 2007-07-31 02:10 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-08-15 05:57 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-10-09 06:34 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-11-22 06:25 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-12-09 02:15 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2007-12-17 19:33 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2008-01-07 00:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2008-01-26 06:27 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2008-02-03 12:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2008-02-03 23:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2008-02-04 15:18 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2008-03-03 05:28 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
222 | 2008-05-28 06:43 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2008-07-15 18:17 | Undetermined | Undetermined | 1 | YSA | 0 | 0
222 | 2008-08-29 10:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2008-09-13 18:44 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2008-12-10 21:10 | Equipment | Cutout failure | 0 | YSA | 1 | 0
222 | 2009-02-05 21:29 | Weather | Wind - wires slap/pole down | 0 | YSA | 0 | 0
222 | 2009-03-01 14:48 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2009-04-08 07:48 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2009-10-19 08:24 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2009-11-09 16:50 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2009-12-10 17:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-01-05 15:36 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2010-01-11 06:32 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2010-01-19 14:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-01-21 13:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-02-05 06:23 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2010-04-04 09:34 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2010-08-14 14:31 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2010-08-23 12:11 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2010-09-30 11:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-09-30 12:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-09-30 13:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-09-30 19:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-09-30 21:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-10-19 12:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2010-10-19 13:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 0 | 0
222 | 2011-02-02 07:18 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0
222 | 2011-04-27 17:00 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
222 | 2011-08-11 23:18 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2011-11-10 16:25 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2011-12-23 06:26 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2012-02-29 06:53 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2012-06-30 07:50 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2012-08-13 08:26 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2012-10-09 07:42 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2012-10-18 14:20 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-01-10 20:42 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-02-05 06:48 | Equipment | Insulator/pin failure/wire floating | 0 | YSA | 0 | 0
222 | 2013-02-25 15:43 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-03-09 04:51 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-03-13 06:41 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-03-19 08:18 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-09-17 06:30 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-10-08 11:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA | 0 | 0
222 | 2013-10-30 10:40 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-12-06 10:14 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2013-12-06 14:50 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-01-09 06:25 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-01-16 06:24 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-02-08 09:48 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-04-26 01:43 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-09-04 07:16 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-10-28 06:34 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2014-10-28 19:24 | Equipment | Crossarm failure | 0 | YSA | 0 | 0
222 | 2014-11-14 09:05 | Equipment | Conductor failure/wire down | 0 | YSA | 0 | 0
222 | 2014-12-10 07:56 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2015-01-05 09:51 | Undetermined | Undetermined | 0 | YSA | 0 | 0
222 | 2015-01-15 12:38 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA | 0 | 0
233 | 2005-04-08 20:28 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2005-06-09 10:37 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2005-08-05 11:27 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2006-08-10 18:32 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2006-09-05 10:07 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK | 0 | 0
233 | 2007-01-27 11:06 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2007-03-11 12:45 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2007-04-26 11:20 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2007-07-17 19:13 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2008-09-19 18:10 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
233 | 2008-12-15 17:51 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2009-01-10 20:26 | Undetermined | Undetermined | 0 | FBK | 1 | 0
233 | 2009-07-18 05:40 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2010-01-02 07:55 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
233 | 2010-06-28 16:45 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
233 | 2010-07-20 06:22 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2010-10-19 03:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
233 | 2011-07-25 05:50 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2011-09-05 04:52 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2011-09-12 18:39 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2012-06-12 16:13 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2012-08-06 17:55 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2012-08-18 17:03 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2013-01-10 14:05 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2013-02-19 23:09 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2013-04-23 14:22 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2013-07-18 08:55 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2013-09-04 11:39 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK | 0 | 0
233 | 2013-11-07 17:25 | Undetermined | Undetermined | 0 | FBK | 0 | 0
233 | 2013-12-06 07:47 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
233 | 2014-02-28 13:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
233 | 2014-02-28 20:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
233 | 2014-04-01 14:30 | Equipment | Conductor contact/wire slap | 0 | FBK | 0 | 0
233 | 2014-04-01 15:34 | Equipment | Conductor contact/wire slap | 0 | FBK | 0 | 0
233 | 2014-12-16 22:41 | Equipment | Pole broke/rotted/on fire | 0 | FBK | 0 | 0
235 | 2005-02-25 06:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
235 | 2007-10-22 08:05 | Weather | Wind - wires slap/pole down | 0 | RAM | 1 | 0
235 | 2008-01-08 10:11 | Undetermined | Undetermined | 0 | RAM | 0 | 0
235 | 2008-11-16 10:26 | Undetermined | Undetermined | 0 | RAM | 0 | 0
235 | 2010-09-30 12:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
235 | 2010-10-28 11:27 | Equipment | Cutout failure | 0 | RAM | 0 | 0
235 | 2011-06-26 16:57 | Undetermined | Undetermined | 0 | RAM | 0 | 0
235 | 2011-07-01 07:01 | Undetermined | Undetermined | 0 | RAM | 0 | 0
235 | 2011-11-01 19:29 | Undetermined | Undetermined | 0 | RAM | 0 | 0
235 | 2012-06-28 18:41 | Undetermined | Undetermined | 0 | RAM | 0 | 0
235 | 2012-08-09 13:51 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2006-12-21 00:47 | Equipment | Conductor failure/wire down | 0 | RAM | 0 | 0
236 | 2007-02-19 19:08 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2007-03-04 10:39 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RAM | 1 | 0
236 | 2007-05-05 09:11 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2007-11-08 13:23 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2007-11-28 08:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2007-11-28 14:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2007-11-30 09:10 | Equipment | Pole broke/rotted/on fire | 0 | RAM | 0 | 0
236 | 2007-12-04 18:22 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2007-12-31 19:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2007-12-31 21:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2008-01-01 02:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0
236 | 2008-01-01 03:43 | Equipment | Insulator/pin failure/wire floating | 0 | RAM | 1 | 0
236 | 2008-01-01 05:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0
236 | 2008-01-01 07:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0
236 | 2008-01-01 08:17 | Weather | Wind - wires slap/pole down | 0 | RAM | 1 | 1
236 | 2008-03-10 18:50 | Weather | Wind - wires slap/pole down | 0 | RAM | 0 | 0
236 | 2008-04-11 18:06 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2008-07-23 06:31 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2009-05-04 16:58 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2009-06-22 07:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RAM | 0 | 0
236 | 2009-12-07 13:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2009-12-13 00:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2010-01-21 06:44 | Weather | Wind - wires slap/pole down | 0 | RAM | 0 | 0
236 | 2010-04-21 22:41 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2010-10-27 14:58 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2011-02-21 12:33 | Equipment | Conductor failure/wire down | 0 | RAM | 0 | 0
236 | 2011-04-05 21:15 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2011-05-04 22:52 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2011-08-03 21:13 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2011-11-12 17:07 | Equipment | Hardware failure | 0 | RAM | 0 | 0
236 | 2012-05-27 01:48 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2012-05-28 13:44 | Equipment | Insulator/pin failure/wire floating | 0 | RAM | 0 | 0
236 | 2012-05-28 17:02 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2012-06-26 12:45 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2012-11-09 01:19 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2013-06-19 05:55 | Undetermined | Undetermined | 0 | RAM | 0 | 0
236 | 2014-02-28 12:29 | Weather | Wind - wires slap/pole down | 0 | RAM | 0 | 0
236 | 2014-04-30 10:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0
236 | 2014-05-13 10:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 0 | 0
236 | 2014-05-14 10:04 | Weather | Wind - wires slap/pole down | 0 | RAM | 0 | 0
236 | 2014-08-04 00:38 | Undetermined | Undetermined | 0 | RAM | 0 | 0
237 | 2005-02-24 15:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS | 0 | 0
237 | 2005-07-12 16:20 | Equipment | Crossarm failure | 1 | GOS | 0 | 0
237 | 2005-07-16 12:02 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2005-08-13 06:52 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2006-04-12 18:17 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2006-04-24 11:05 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2007-05-16 18:20 | Equipment | Crossarm failure | 0 | GOS | 0 | 0
237 | 2007-11-11 08:36 | Equipment | Insulator/pin failure/wire floating | 0 | GOS | 0 | 0
237 | 2007-11-13 08:43 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2007-12-02 12:12 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2007-12-31 22:21 | Weather | Wind - wires slap/pole down | 0 | GOS | 0 | 0
237 | 2008-03-03 07:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS | 0 | 0
237 | 2008-03-03 08:04 | Weather | Wind - wires slap/pole down | 0 | GOS | 0 | 0
237 | 2008-04-13 19:02 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS | 0 | 0
237 | 2008-10-03 12:27 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2008-10-04 05:10 | Equipment | Conductor contact/wire slap | 0 | GOS | 0 | 0
237 | 2008-10-31 10:41 | Equipment | Conductor contact/wire slap | 0 | GOS | 0 | 0
237 | 2008-12-09 15:25 | Undetermined | Undetermined | 0 | GOS | 1 | 0
237 | 2008-12-15 09:58 | Equipment | Conductor contact/wire slap | 0 | GOS | 0 | 0
237 | 2010-01-19 14:05 | Weather | Wind - wires slap/pole down | 0 | GOS | 0 | 0
237 | 2010-01-21 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS | 0 | 0
237 | 2010-02-05 00:49 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2010-10-07 17:31 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2011-02-02 08:12 | Weather | Wind - wires slap/pole down | 0 | GOS | 1 | 0
237 | 2011-04-28 00:58 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2012-03-29 14:14 | Equipment | Cutout failure | 0 | GOS | 0 | 0
237 | 2012-09-10 15:11 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2012-11-10 12:00 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2013-06-11 04:28 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2013-08-29 14:16 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2014-05-14 08:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | GOS | 0 | 0
237 | 2014-09-25 10:20 | Undetermined | Undetermined | 0 | GOS | 0 | 0
237 | 2015-02-23 08:12 | Equipment | Cutout failure | 0 | GOS | 0 | 0
239 | 2005-04-21 12:53 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
239 | 2005-09-05 13:48 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2005-11-29 12:10 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2005-12-16 18:44 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-01-06 22:24 | Undetermined | Undetermined | 0 | FBK | 1 | 0
239 | 2006-01-23 08:31 | Undetermined | Undetermined | 0 | FBK | 1 | 0
239 | 2006-01-23 09:30 | Weather | Wind - wires slap/pole down | 0 | FBK | 1 | 0
239 | 2006-02-06 17:43 | Undetermined | Undetermined | 0 | FBK | 1 | 0
239 | 2006-02-26 21:40 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-06-06 23:07 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-08-18 08:47 | Equipment | Pole broke/rotted/on fire | 0 | FBK | 0 | 0
239 | 2006-10-10 09:25 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-11-19 15:45 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-11-21 07:26 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-11-26 09:50 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-11-28 22:15 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2006-11-29 11:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
239 | 2006-12-09 08:43 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2007-10-29 11:03 | Equipment | Conductor contact/wire slap | 0 | FBK | 0 | 0
239 | 2009-06-03 13:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
239 | 2009-11-28 14:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | FBK | 0 | 0
239 | 2009-12-07 17:08 | Weather | Wind - wires slap/pole down | 0 | FBK | 0 | 0
239 | 2010-01-21 22:58 | Weather | Wind - wires slap/pole down | 0 | FBK | 0 | 0
239 | 2010-02-27 19:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK | 0 | 0
239 | 2010-04-02 20:09 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2010-06-01 08:48 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2010-10-13 13:57 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2011-02-19 22:43 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
239 | 2011-03-01 08:45 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
239 | 2012-03-20 06:38 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2012-08-15 19:26 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2012-09-04 19:03 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK | 0 | 0
239 | 2012-12-31 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | FBK | 0 | 0
239 | 2013-09-20 18:43 | Undetermined | Undetermined | 0 | FBK | 0 | 0
239 | 2013-12-07 14:59 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
239 | 2014-07-25 21:31 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
239 | 2014-09-16 15:52 | Equipment | Conductor failure/wire down | 0 | FBK | 0 | 0
239 | 2015-01-08 13:56 | Undetermined | Undetermined | 0 | FBK | 0 | 0
240 | 2005-07-23 06:07 | Weather | Wind - wires slap/pole down | 0 | BVY | 0 | 0
240 | 2005-07-27 06:03 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2005-11-10 13:11 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2006-03-05 09:02 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2006-09-08 13:11 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2006-09-20 11:34 | Equipment | Conductor failure/wire down | 0 | BVY | 0 | 0
240 | 2006-11-27 12:03 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2008-12-15 14:19 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2009-02-09 17:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2009-12-07 15:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2010-01-19 15:12 | Weather | Wind - wires slap/pole down | 0 | BVY | 0 | 0
240 | 2010-09-30 12:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2010-09-30 13:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2010-09-30 17:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2010-09-30 22:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2010-10-25 13:35 | Equipment | Crossarm failure | 0 | BVY | 0 | 0
240 | 2010-11-22 03:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVY | 0 | 0
240 | 2011-01-23 07:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 1 | 0
240 | 2011-02-02 13:11 | Weather | Wind - wires slap/pole down | 0 | BVY | 1 | 0
240 | 2011-03-28 09:03 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2012-03-01 09:25 | Equipment | Conductor failure/wire down | 0 | BVY | 0 | 0
240 | 2012-03-02 08:59 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2012-03-18 11:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2012-03-18 12:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2012-09-14 08:38 | Weather | Wind - wires slap/pole down | 0 | BVY | 0 | 0
240 | 2012-09-14 11:13 | Equipment | Conductor contact/wire slap | 0 | BVY | 0 | 0
240 | 2013-02-08 06:51 | Foreign Object | Flashover/vegetation | 0 | BVY | 0 | 0
240 | 2013-06-18 08:21 | Equipment | Conductor failure/wire down | 0 | BVY | 0 | 0
240 | 2013-10-04 01:18 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2013-10-04 07:06 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2013-12-18 10:40 | Undetermined | Undetermined | 0 | BVY | 0 | 0
240 | 2014-02-06 19:30 | Equipment | Cutout failure | 0 | BVY | 0 | 0
240 | 2014-02-28 18:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
240 | 2014-04-30 13:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 1 | 0
240 | 2015-01-25 10:08 | Undetermined | Undetermined | 0 | BVY | 1 | 0
243 | 2005-07-13 13:50 | Equipment | Cutout failure | 1 | BVY | 0 | 0
243 | 2006-01-24 22:28 | Equipment | Cutout failure | 0 | BVY | 0 | 0
243 | 2007-04-22 15:33 | Undetermined | Undetermined | 0 | BVY | 0 | 0
243 | 2007-05-27 19:00 | Undetermined | Undetermined | 0 | BVY | 0 | 0
243 | 2009-05-08 04:21 | Undetermined | Undetermined | 0 | BVY | 0 | 0
243 | 2013-10-29 10:32 | Equipment | Pole broke/rotted/on fire | 0 | BVY | 0 | 0
246 | 2005-01-29 15:25 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2006-07-23 16:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
246 | 2007-11-08 03:57 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2008-02-29 12:32 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2008-03-30 00:42 | Equipment | Insulator/pin failure/wire floating | 0 | BVY | 0 | 0
246 | 2010-08-19 10:36 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2010-09-16 17:54 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2010-09-26 14:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
246 | 2010-09-30 13:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 0 | 0
246 | 2011-12-16 09:20 | Equipment | Pole broke/rotted/on fire | 0 | BVY | 0 | 0
246 | 2012-01-23 15:04 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2013-03-20 20:10 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2013-04-05 00:32 | Equipment | Conductor failure/wire down | 0 | BVY | 0 | 0
246 | 2014-01-15 06:53 | Undetermined | Undetermined | 0 | BVY | 0 | 0
246 | 2014-06-04 15:55 | Equipment | Crossarm failure | 0 | BVY | 0 | 0
246 | 2015-03-01 20:40 | Undetermined | Undetermined | 0 | BVY | 0 | 0
283 | 2007-06-11 08:31 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2007-06-17 06:55 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD | 0 | 0
283 | 2007-08-17 22:37 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2007-11-23 19:10 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2008-05-13 07:50 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2008-08-14 15:57 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2009-12-08 08:36 | Weather | Wind - wires slap/pole down | 0 | LLD | 0 | 0
283 | 2012-05-28 18:21 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2012-12-07 20:36 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD | 0 | 0
283 | 2013-05-12 13:08 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLD | 0 | 0
283 | 2013-06-22 07:54 | Equipment | Cutout failure | 0 | LLD | 0 | 0
283 | 2013-06-22 08:50 | Equipment | Cutout failure | 0 | LLD | 0 | 0
283 | 2013-07-21 16:27 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2014-12-04 05:21 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2014-12-12 11:27 | Undetermined | Undetermined | 0 | LLD | 0 | 0
283 | 2015-02-17 09:05 | Equipment | Cutout failure | 0 | LLD | 0 | 0
305 | 2006-08-29 11:25 | Equipment | Cutout failure | 0 | RSF | 0 | 0
305 | 2008-12-19 00:37 | Undetermined | Undetermined | 0 | RSF | 0 | 0
305 | 2009-02-25 06:07 | Undetermined | Undetermined | 0 | RSF | 0 | 0
305 | 2009-07-13 22:07 | Equipment | Conductor failure/wire down | 1 | RSF | 0 | 0
305 | 2009-12-07 17:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RSF | 0 | 0
305 | 2012-08-14 14:46 | Undetermined | Undetermined | 0 | RSF | 0 | 0
305 | 2013-02-01 16:15 | Undetermined | Undetermined | 0 | RSF | 0 | 0
305 | 2013-05-02 10:24 | Equipment | Cutout failure | 0 | RSF | 0 | 0
307 | 2009-02-23 19:29 | Undetermined | Undetermined | 0 | RSF | 0 | 0
311 | 2010-01-21 15:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP | 0 | 0
311 | 2010-09-25 23:18 | Undetermined | Undetermined | 0 | CAP | 0 | 0
311 | 2011-10-02 15:17 | Undetermined | Undetermined | 0 | CAP | 0 | 0
311 | 2011-11-17 12:23 | Undetermined | Undetermined | 0 | CAP | 0 | 0
311 | 2014-12-12 04:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP | 0 | 0
311 | 2014-12-30 21:30 | Equipment | Conductor failure/wire down | 0 | CAP | 0 | 0
320 | 2014-09-24 20:36 | Undetermined | Undetermined | 0 | MIG | 0 | 0
321 | 2007-02-05 11:21 | Equipment | Cutout failure | 0 | MIG | 0 | 0
321 | 2009-12-07 17:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MIG | 0 | 0
321 | 2010-01-19 13:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MIG | 0 | 0
321 | 2010-08-24 23:56 | Undetermined | Undetermined | 0 | MIG | 0 | 0
321 | 2014-03-10 16:19 | Equipment | Cutout failure | 0 | MIG | 0 | 0
322 | 2005-10-31 06:08 | Undetermined | Undetermined | 0 | MIG | 0 | 0
322 | 2008-11-18 15:54 | Undetermined | Undetermined | 0 | MIG | 0 | 0
322 | 2008-11-29 18:53 | Undetermined | Undetermined | 0 | MIG | 0 | 0
322 | 2008-12-16 10:26 | Equipment | Crossarm failure | 0 | MIG | 0 | 0
322 | 2008-12-28 05:17 | Undetermined | Undetermined | 0 | MIG | 0 | 0
322 | 2011-03-03 13:02 | Undetermined | Undetermined | 0 | MIG | 0 | 0
322 | 2013-04-01 22:33 | Undetermined | Undetermined | 0 | MIG | 0 | 0
322 | 2014-08-22 12:18 | Equipment | Cutout failure | 0 | MIG | 0 | 0
322 | 2014-10-05 17:15 | Undetermined | Undetermined | 0 | MIG | 0 | 0
323 | 2007-01-04 21:03 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MIG | 0 | 0
323 | 2014-04-10 05:54 | Undetermined | Undetermined | 0 | MIG | 0 | 0
323 | 2014-09-05 04:29 | Undetermined | Undetermined | 0 | MIG | 0 | 0
323 | 2015-02-03 23:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MIG | 0 | 0
324 | 2013-04-22 11:34 | Undetermined | Undetermined | 0 | MIG | 0 | 0
324 | 2014-04-15 05:54 | Equipment | Guy wire failure | 0 | MIG | 0 | 0
324 | 2014-04-15 10:27 | Equipment | Guy wire failure | 0 | MIG | 0 | 0
339 | 2005-03-24 09:15 | Equipment | Pole broke/rotted/on fire | 0 | CAP | 0 | 0
339 | 2006-11-11 10:24 | Undetermined | Undetermined | 0 | CAP | 0 | 0
339 | 2010-10-19 07:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CAP | 0 | 0
350 | 2005-01-20 10:38 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2005-09-20 01:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2005-12-05 12:20 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2006-01-02 10:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2006-01-02 20:11 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2006-01-02 23:26 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2006-01-10 19:41 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2006-02-28 06:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2006-03-10 13:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2006-03-11 07:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2006-06-26 14:29 | Equipment | Insulator/pin failure/wire floating | 0 | LLC | 0 | 0
350 | 2006-06-28 18:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
350 | 2006-08-30 05:50 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2006-12-19 15:56 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2007-05-18 13:36 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
350 | 2007-06-16 22:36 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2007-10-13 05:27 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2008-01-27 05:35 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2008-02-19 10:00 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2008-06-07 10:50 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2008-07-19 10:49 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2008-09-02 12:53 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2008-11-06 10:46 | Undetermined | Undetermined | 0 | LLC | 1 | 0
350 | 2008-12-18 02:51 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2009-02-09 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2009-02-16 22:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
350 | 2009-07-22 23:08 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
350 | 2009-08-05 13:40 | Equipment | Crossarm failure | 0 | LLC | 0 | 0
350 | 2009-10-14 07:00 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2009-11-29 09:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2009-12-07 14:21 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2009-12-07 17:35 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2009-12-07 21:40 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2009-12-09 11:18 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2009-12-13 09:23 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2010-01-12 14:14 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2010-01-19 14:45 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2010-01-21 12:23 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2010-01-21 15:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2010-01-22 08:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2010-01-31 10:21 | Equipment | Crossarm failure | 0 | LLC | 0 | 0
350 | 2010-05-13 06:03 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2010-05-25 09:21 | Equipment | Hardware failure | 0 | LLC | 0 | 0
350 | 2010-06-18 11:52 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2010-10-19 02:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2010-10-19 05:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2010-12-20 05:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2011-03-09 14:25 | Equipment | Conductor failure/wire down | 0 | LLC | 0 | 0
350 | 2011-05-20 12:33 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2011-06-29 19:41 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2011-09-05 10:42 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
350 | 2011-10-12 13:53 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2012-02-14 06:04 | Foreign Object | Flashover/vegetation | 0 | LLC | 0 | 0
350 | 2012-03-12 13:19 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
350 | 2012-06-30 12:41 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2012-07-28 09:50 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2012-12-30 11:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2013-03-19 16:48 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2013-03-27 08:55 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2013-06-07 06:34 | Equipment | Insulator/pin failure/wire floating | 0 | LLC | 0 | 0
350 | 2014-03-01 02:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
350 | 2014-04-23 12:17 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
350 | 2014-09-17 15:22 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2014-12-03 00:31 | Undetermined | Undetermined | 0 | LLC | 0 | 0
350 | 2014-12-17 04:08 | Undetermined | Undetermined | 0 | LLC | 0 | 0
351 | 2005-11-27 04:35 | Equipment | Conductor failure/wire down | 0 | TLK | 0 | 0
351 | 2006-03-18 12:23 | Weather | Wind - wires slap/pole down | 0 | TLK | 0 | 0
351 | 2006-11-29 17:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 0 | 0
351 | 2007-01-05 17:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 1 | 0
351 | 2007-10-22 03:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 1 | 0
351 | 2008-06-26 17:29 | Undetermined | Undetermined | 0 | TLK | 0 | 0
351 | 2008-12-15 01:36 | Equipment | Connector/jumper/splice/elbow/rack | 0 | TLK | 0 | 0
351 | 2009-11-30 01:04 | Undetermined | Undetermined | 0 | TLK | 0 | 0
351 | 2010-01-21 14:28 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 0 | 0
351 | 2012-04-13 14:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 0 | 0
351 | 2012-04-13 16:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 0 | 0
351 | 2013-03-08 13:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | TLK | 0 | 0
351 | 2013-03-20 10:27 | Equipment | Connector/jumper/splice/elbow/rack | 0 | TLK | 0 | 0
351 | 2014-12-26 08:50 | Undetermined | Undetermined | 0 | TLK | 0 | 0
352 | 2005-08-06 02:45 | Undetermined | Undetermined | 0 | LLC | 0 | 0
352 | 2006-01-02 12:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
352 | 2006-07-30 02:48 | Undetermined | Undetermined | 0 | LLC | 0 | 0
352 | 2006-08-07 06:14 | Undetermined | Undetermined | 0 | LLC | 0 | 0
352 | 2006-11-25 10:57 | Undetermined | Undetermined | 0 | LLC | 0 | 0
352 | 2006-12-27 11:49 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
352 | 2006-12-27 13:56 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
352 | 2006-12-27 15:07 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
352 | 2007-10-31 10:10 | Equipment | Conductor failure/wire down | 0 | LLC | 0 | 0
352 | 2007-12-04 15:57 | Undetermined | Undetermined | 0 | LLC | 0 | 0
352 | 2010-01-21 23:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
352 | 2012-09-09 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
352 | 2013-11-10 11:18 | Equipment | Hardware failure | 0 | LLC | 0 | 0
352 | 2014-02-15 10:17 | Undetermined | Undetermined | 0 | LLC | 0 | 0
352 | 2015-01-19 22:03 | Undetermined | Undetermined | 0 | LLC | 0 | 0
353 | 2006-07-09 19:08 | Equipment | Conductor failure/wire down | 1 | LLC | 0 | 0
353 | 2006-10-13 19:54 | Equipment | Crossarm failure | 0 | LLC | 0 | 0
353 | 2009-10-28 10:20 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
353 | 2009-10-28 16:51 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
353 | 2009-11-28 11:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
353 | 2010-01-21 13:23 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
353 | 2010-10-06 04:22 | Equipment | Insulator/pin failure/wire floating | 0 | LLC | 0 | 0
353 | 2012-09-09 16:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
353 | 2012-09-10 05:17 | Undetermined | Undetermined | 0 | LLC | 0 | 0
353 | 2012-12-13 12:42 | Equipment | Crossarm failure | 0 | LLC | 0 | 0
353 | 2012-12-13 12:48 | Equipment | Crossarm failure | 0 | LLC | 0 | 1
353 | 2014-05-14 08:13 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
353 | 2014-05-15 16:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
353 | 2014-07-24 17:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
354 | 2005-12-07 07:56 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2006-03-26 14:38 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2006-12-03 10:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 1 | 0
354 | 2007-03-08 16:40 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2008-11-26 05:42 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
354 | 2009-01-13 13:10 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2009-12-07 14:42 | Weather | Wind - wires slap/pole down | 0 | LLC | 0 | 0
354 | 2010-01-19 04:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 0 | 0
354 | 2010-08-13 13:02 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2010-11-27 07:30 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
354 | 2011-01-27 07:30 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2011-11-12 02:03 | Equipment | Cutout failure | 0 | LLC | 0 | 0
354 | 2012-10-05 10:31 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
354 | 2012-10-05 16:04 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2012-10-30 07:13 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2012-12-20 01:24 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2012-12-20 07:06 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2013-01-11 07:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
354 | 2014-02-16 13:40 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LLC | 0 | 0
354 | 2014-03-05 09:49 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2014-06-14 11:08 | Undetermined | Undetermined | 0 | LLC | 0 | 0
354 | 2014-08-21 15:09 | Undetermined | Undetermined | 0 | LLC | 0 | 0
355 | 2005-02-04 09:31 | Equipment | Insulator/pin failure/wire floating | 0 | ANE | 0 | 0
355 | 2007-10-22 23:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0
355 | 2012-11-06 09:11 | Undetermined | Undetermined | 0 | ANE | 0 | 0
355 | 2012-12-13 02:12 | Weather | Wind - wires slap/pole down | 0 | ANE | 0 | 0
355 | 2013-06-22 21:50 | Equipment | Cutout failure | 0 | ANE | 0 | 0
355 | 2014-12-03 10:01 | Undetermined | Undetermined | 0 | ANE | 0 | 0
356 | 2005-01-04 19:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2006-02-08 12:31 | Undetermined | Undetermined | 0 | WAL | 1 | 0
356 | 2006-07-07 16:33 | Undetermined | Undetermined | 1 | WAL | 0 | 0
356 | 2007-10-22 16:00 | Weather | Wind - wires slap/pole down | 0 | WAL | 1 | 0
356 | 2009-04-11 14:45 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2009-10-28 16:36 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2009-12-07 17:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2009-12-22 06:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2010-01-19 16:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2010-01-20 18:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2010-03-09 12:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2010-03-09 12:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WAL | 0 | 0
356 | 2010-04-12 15:44 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2010-04-21 19:02 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2010-08-11 20:25 | Equipment | Pole broke/rotted/on fire | 0 | WAL | 0 | 0
356 | 2010-08-24 19:12 | Equipment | Crossarm failure | 0 | WAL | 0 | 0
356 | 2010-09-22 16:16 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2011-05-21 09:03 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2012-09-02 16:44 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2013-04-18 16:57 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2013-06-19 23:11 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2013-06-23 14:28 | Equipment | Conductor failure/wire down | 0 | WAL | 0 | 0
356 | 2014-12-02 19:52 | Undetermined | Undetermined | 0 | WAL | 0 | 0
356 | 2015-02-21 06:40 | Undetermined | Undetermined | 0 | WAL | 0 | 0
357 | 2005-04-28 12:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD | 0 | 0
357 | 2007-01-30 19:52 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2007-03-02 16:34 | Undetermined | Undetermined | 0 | PVD | 1 | 0
357 | 2007-05-15 12:43 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2007-10-22 07:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PVD | 1 | 0
357 | 2008-11-09 11:40 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2009-10-06 10:18 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2009-11-26 10:54 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2009-12-07 16:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD | 0 | 0
357 | 2010-02-21 12:17 | Foreign Object | Flashover/vegetation | 0 | PVD | 0 | 0
357 | 2010-08-21 21:28 | Equipment | Cutout failure | 0 | PVD | 0 | 0
357 | 2010-09-30 17:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD | 0 | 0
357 | 2010-10-17 15:15 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2011-07-30 06:10 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2011-10-14 08:11 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2012-05-24 18:55 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2013-05-07 03:41 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2013-05-20 16:29 | Equipment | Cutout failure | 0 | PVD | 0 | 0
357 | 2014-03-01 17:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PVD | 0 | 0
357 | 2014-06-29 04:54 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2014-12-02 20:40 | Undetermined | Undetermined | 0 | PVD | 0 | 0
357 | 2015-03-13 12:30 | Undetermined | Undetermined | 0 | PVD | 0 | 0
358 | 2005-01-12 12:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
358 | 2005-10-21 10:49 | Equipment | Crossarm failure | 0 | ANE | 0 | 0
358 | 2006-03-11 15:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
358 | 2006-11-29 17:29 | Weather | Wind - wires slap/pole down | 0 | ANE | 0 | 0
358 | 2007-10-21 21:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0
358 | 2007-10-22 06:41 | Weather | Wind - wires slap/pole down | 0 | ANE | 1 | 0
358 | 2007-11-30 15:44 | Weather | Wind - wires slap/pole down | 0 | ANE | 0 | 0
358 | 2008-10-14 09:52 | Equipment | Crossarm failure | 0 | ANE | 1 | 0
358 | 2009-01-11 23:13 | Undetermined | Undetermined | 0 | ANE | 1 | 0
358 | 2009-11-28 09:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
358 | 2010-10-26 09:46 | Undetermined | Undetermined | 0 | ANE | 0 | 0
358 | 2010-12-23 23:15 | Weather | Wind - wires slap/pole down | 0 | ANE | 0 | 0
358 | 2011-12-09 15:49 | Undetermined | Undetermined | 0 | ANE | 0 | 0
358 | 2014-05-14 08:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 0 | 0
374 | 2005-10-12 19:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | KSAN | 0 | 0
374 | 2006-08-05 18:48 | Undetermined | Undetermined | 0 | KSAN | 0 | 0
374 | 2007-04-24 14:39 | Equipment | Crossarm failure | 0 | KSAN | 0 | 0
374 | 2008-10-04 20:44 | Equipment | Cutout failure | 0 | KSAN | 0 | 0
374 | 2010-04-18 10:48 | Undetermined | Undetermined | 0 | KSAN | 0 | 0
374 | 2013-06-09 17:59 | Undetermined | Undetermined | 0 | KSAN | 0 | 0
374 | 2014-06-04 09:29 | Undetermined | Undetermined | 0 | KSAN | 0 | 0
378 | 2011-04-10 17:12 | Undetermined | Undetermined | 0 | KSAN | 0 | 0
411 | 2005-09-20 09:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst | 0 | 0
411 | 2005-09-20 12:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst | 0 | 0
411 | 2005-10-05 15:57 | Undetermined | Undetermined | 0 | cst | 0 | 0
411 | 2007-10-23 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst | 1 | 0
411 | 2008-07-09 19:23 | Equipment | Connector/jumper/splice/elbow/rack | 1 | cst | 0 | 0
411 | 2009-01-29 15:18 | Equipment | Conductor contact/wire slap | 0 | cst | 0 | 0
411 | 2009-12-07 17:36 | Weather | Wind - wires slap/pole down | 0 | cst | 0 | 0
411 | 2010-01-19 15:03 | Weather | Wind - wires slap/pole down | 0 | cst | 0 | 0
411 | 2010-01-20 08:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst | 0 | 0
411 | 2010-01-21 06:51 | Weather | Wind - wires slap/pole down | 0 | cst | 0 | 0
411 | 2010-01-21 13:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst | 0 | 0
411 | 2011-07-28 13:09 | Undetermined | Undetermined | 0 | cst | 0 | 0
411 | 2012-12-27 20:44 | Equipment | Guy wire failure | 0 | cst | 0 | 0
411 | 2013-01-25 06:08 | Foreign Object | Flashover/vegetation | 0 | cst | 0 | 0
411 | 2013-09-15 17:44 | Undetermined | Undetermined | 0 | cst | 0 | 0
411 | 2013-11-21 07:33 | Weather | Circuit Flashover/fog/foreign object | 0 | cst | 0 | 0
440 | 2005-02-17 09:27 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2005-08-11 12:20 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2006-01-05 20:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 1 | 0
440 | 2007-03-08 08:44 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2007-08-01 12:45 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2007-11-15 13:08 | Equipment | Pole broke/rotted/on fire | 0 | LAG | 0 | 0
440 | 2008-01-06 13:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 0 | 0
440 | 2008-12-13 20:31 | Weather | Wind - wires slap/pole down | 0 | LAG | 0 | 0
440 | 2009-02-05 22:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 0 | 0
440 | 2009-12-06 17:55 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2009-12-08 03:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 0 | 0
440 | 2010-08-26 08:49 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2011-04-13 14:40 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2011-07-08 19:12 | Undetermined | Undetermined | 1 | LAG | 0 | 0
440 | 2011-12-03 10:29 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2012-10-18 16:25 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2012-12-14 04:58 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2012-12-14 09:05 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2013-02-15 23:07 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2013-02-16 02:02 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2013-08-27 15:20 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2013-09-06 13:58 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LAG | 0 | 0
440 | 2013-09-10 18:46 | Undetermined | Undetermined | 0 | LAG | 0 | 0
440 | 2014-05-01 09:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 1 | 0
440 | 2014-07-07 19:01 | Undetermined | Undetermined | 1 | LAG | 0 | 0
440 | 2014-07-09 12:51 | Equipment | Pole broke/rotted/on fire | 1 | LAG | 0 | 0
440 | 2014-07-15 01:13 | Equipment | Cutout failure | 1 | LAG | 0 | 0
441 | 2006-03-11 13:22 | Weather | Wind - wires slap/pole down | 0 | LPT | 0 | 0
441 | 2007-03-03 13:13 | Weather | Wind - wires slap/pole down | 0 | LPT | 1 | 0
441 | 2007-10-22 02:39 | Weather | Wind - wires slap/pole down | 0 | LPT | 1 | 0
441 | 2007-11-09 23:12 | Weather | Wind - wires slap/pole down | 0 | LPT | 0 | 0
441 | 2009-03-24 06:45 | Undetermined | Undetermined | 0 | LPT | 0 | 0
441 | 2009-08-27 10:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LPT | 0 | 0
441 | 2011-02-02 08:02 | Weather | Circuit Flashover/fog/foreign object | 0 | LPT | 1 | 0
441 | 2011-05-24 08:17 | Undetermined | Undetermined | 0 | LPT | 0 | 0
441 | 2011-05-26 02:41 | Undetermined | Undetermined | 0 | LPT | 0 | 0
441 | 2011-05-26 13:45 | Undetermined | Undetermined | 0 | LPT | 0 | 0
441 | 2012-02-27 21:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LPT | 0 | 0
441 | 2012-02-27 22:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LPT | 0 | 0
441 | 2012-08-13 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LPT | 0 | 0
441 | 2013-07-20 17:01 | Undetermined | Undetermined | 0 | LPT | 0 | 0
441 | 2014-08-02 08:40 | Undetermined | Undetermined | 0 | LPT | 0 | 0
442 | 2006-03-11 09:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2006-10-20 08:20 | Equipment | Cutout failure | 0 | SRH | 0 | 0
442 | 2007-05-01 11:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2007-07-19 09:44 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2007-10-22 00:11 | Weather | Wind - wires slap/pole down | 0 | SRH | 1 | 0
442 | 2007-10-22 01:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 1 | 0
442 | 2007-10-22 17:07 | Weather | Wind - wires slap/pole down | 0 | SRH | 1 | 0
442 | 2008-01-14 07:36 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2008-02-03 13:46 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2008-02-03 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2008-07-13 09:11 | Undetermined | Undetermined | 1 | SRH | 0 | 0
442 | 2009-01-10 21:02 | Weather | Wind - wires slap/pole down | 0 | SRH | 1 | 0
442 | 2009-12-08 00:51 | Weather | Wind - wires slap/pole down | 0 | SRH | 0 | 0
442 | 2010-08-09 11:15 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2010-09-19 04:33 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SRH | 0 | 0
442 | 2011-01-31 06:20 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2011-07-05 18:27 | Undetermined | Undetermined | 1 | SRH | 0 | 0
442 | 2011-08-27 13:01 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2012-02-14 09:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2012-02-28 00:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2012-02-28 02:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2012-02-28 02:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 1
442 | 2012-02-28 03:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2012-03-18 05:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 0
442 | 2012-03-18 12:24 | Weather | Wind - wires slap/pole down | 0 | SRH | 0 | 0
442 | 2013-07-21 13:59 | Undetermined | Undetermined | 0 | SRH | 0 | 0
442 | 2014-05-01 04:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 1 | 0
442 | 2015-02-11 14:30 | Equipment | Conductor failure/wire down | 0 | SRH | 0 | 0
444 | 2005-02-22 07:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
444 | 2005-04-09 00:29 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2005-07-21 17:32 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2005-07-22 14:34 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2006-10-06 06:04 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2007-01-11 20:50 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2007-01-12 09:00 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2007-03-02 19:57 | Undetermined | Undetermined | 0 | BVD | 1 | 0
444 | 2007-06-16 14:48 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2008-05-20 11:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
444 | 2008-05-20 13:50 | Equipment | Insulator/pin failure/wire floating | 0 | BVD | 0 | 0
444 | 2008-12-13 17:40 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2009-05-29 19:55 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2009-06-29 14:16 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2009-08-26 15:50 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD | 0 | 0
444 | 2009-12-07 20:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
444 | 2009-12-27 03:19 | Equipment | Conductor failure/wire down | 0 | BVD | 0 | 0
444 | 2010-03-20 01:11 | Equipment | Conductor failure/wire down | 0 | BVD | 0 | 0
444 | 2010-06-18 11:40 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2010-09-27 09:27 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2010-10-04 09:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
444 | 2011-01-11 17:50 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2011-03-08 15:55 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2011-10-12 00:44 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2012-02-27 22:05 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2012-03-07 07:19 | Equipment | Cutout failure | 0 | BVD | 0 | 0
444 | 2012-03-18 22:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
444 | 2012-03-19 14:17 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
444 | 2012-03-25 22:59 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD | 0 | 0
444 | 2012-07-17 22:29 | Equipment | Conductor failure/wire down | 0 | BVD | 0 | 0
444 | 2012-08-13 18:37 | Equipment | Insulator/pin failure/wire floating | 0 | BVD | 0 | 0
444 | 2012-11-08 02:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD | 0 | 0
444 | 2012-11-13 10:38 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2013-03-28 14:02 | Foreign Object | Flashover/vegetation | 0 | BVD | 0 | 0
444 | 2013-06-03 17:02 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2013-07-20 17:52 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2013-09-13 04:23 | Equipment | Hardware failure | 0 | BVD | 0 | 0
444 | 2014-03-06 16:03 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2014-03-10 07:12 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2014-04-09 10:51 | Undetermined | Undetermined | 0 | BVD | 0 | 0
444 | 2014-04-19 16:26 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2005-02-05 16:53 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2005-03-23 11:31 | Equipment | Conductor failure/wire down | 0 | BVD | 0 | 0
445 | 2005-04-27 13:50 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2005-07-24 17:23 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2005-10-01 07:50 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2005-11-28 09:57 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2005-12-11 07:15 | Equipment | Conductor failure/wire down | 0 | BVD | 0 | 0
445 | 2006-01-23 09:23 | Equipment | Conductor failure/wire down | 0 | BVD | 1 | 0
445 | 2006-03-11 09:15 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2006-07-07 16:04 | Undetermined | Undetermined | 1 | BVD | 0 | 0
445 | 2006-12-27 15:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
445 | 2007-07-10 09:00 | Undetermined | Undetermined | 1 | BVD | 0 | 0
445 | 2007-10-21 20:16 | Weather | Wind - wires slap/pole down | 0 | BVD | 1 | 0
445 | 2007-10-22 08:11 | Weather | Wind - wires slap/pole down | 0 | BVD | 1 | 0
445 | 2007-11-30 17:00 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD | 0 | 0
445 | 2008-02-28 01:09 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2008-07-09 11:22 | Equipment | Connector/jumper/splice/elbow/rack | 1 | BVD | 0 | 0
445 | 2008-12-17 12:55 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2008-12-17 16:36 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2009-05-17 12:30 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2009-08-06 16:19 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2009-10-08 11:21 | Equipment | Crossarm failure | 0 | BVD | 0 | 0
445 | 2009-12-12 03:53 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2010-01-30 08:38 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2010-04-15 07:12 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2010-06-24 10:49 | Equipment | Pole broke/rotted/on fire | 0 | BVD | 0 | 0
445 | 2010-07-06 08:23 | Undetermined | Undetermined | 1 | BVD | 0 | 0
445 | 2010-08-23 17:02 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2010-10-02 02:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
445 | 2010-10-20 14:09 | Equipment | Cutout failure | 0 | BVD | 0 | 0
445 | 2010-11-29 01:24 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2010-12-10 04:58 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2011-01-11 07:20 | Equipment | Conductor failure/wire down | 0 | BVD | 0 | 0
445 | 2011-02-20 03:52 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2011-05-26 09:05 | Equipment | Connector/jumper/splice/elbow/rack | 0 | BVD | 0 | 0
445 | 2011-06-17 03:58 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2011-07-05 17:18 | Undetermined | Undetermined | 1 | BVD | 0 | 0
445 | 2011-07-05 17:27 | Undetermined | Undetermined | 1 | BVD | 0 | 1
445 | 2011-07-18 10:28 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-02-10 04:17 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-02-14 05:35 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2012-02-18 14:01 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-02-27 20:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
445 | 2012-02-27 21:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 1
445 | 2012-02-27 21:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 1
445 | 2012-02-27 21:34 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 1
445 | 2012-02-28 05:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
445 | 2012-03-18 18:33 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2012-03-19 08:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
445 | 2012-04-10 08:48 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-04-14 19:17 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-04-17 09:20 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-04-19 07:51 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2012-06-27 11:52 | Equipment | Pole broke/rotted/on fire | 0 | BVD | 0 | 0
445 | 2012-08-18 15:16 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2013-02-20 02:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 0
445 | 2013-03-22 08:11 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2013-09-20 08:24 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-03-01 00:38 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 0
445 | 2014-03-04 14:37 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-03-10 08:02 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-05-06 04:29 | Equipment | Insulator/pin failure/wire floating | 0 | BVD | 0 | 0
445 | 2014-05-06 07:27 | Equipment | Insulator/pin failure/wire floating | 0 | BVD | 0 | 0
445 | 2014-06-09 06:34 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-06-25 22:17 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-08-20 15:23 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-08-27 01:45 | Undetermined | Undetermined | 0 | BVD | 0 | 0
445 | 2014-11-22 05:53 | Undetermined | Undetermined | 0 | BVD | 0 | 0
448 | 2005-06-25 10:16 | Equipment | Conductor failure/wire down | 0 | WPT | 0 | 0
448 | 2005-08-17 19:19 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2006-09-11 10:07 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2006-11-29 19:36 | Weather | Wind - wires slap/pole down | 0 | WPT | 0 | 0
448 | 2006-12-25 19:21 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2007-05-30 06:21 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2007-10-22 09:57 | Weather | Wind - wires slap/pole down | 0 | WPT | 1 | 0
448 | 2007-10-23 12:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 1 | 0
448 | 2007-11-02 12:25 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2008-03-25 12:29 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2008-09-03 15:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 0 | 0
448 | 2008-09-28 15:43 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2009-01-30 11:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WPT | 0 | 0
448 | 2009-03-31 09:09 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2009-11-28 01:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 0 | 0
448 | 2010-07-03 14:00 | Undetermined | Undetermined | 1 | WPT | 0 | 0
448 | 2011-07-04 15:04 | Undetermined | Undetermined | 1 | WPT | 0 | 0
448 | 2011-08-28 14:52 | Weather | Wind - wires slap/pole down | 0 | WPT | 0 | 0
448 | 2011-10-02 16:52 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2011-10-11 08:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WPT | 0 | 0
448 | 2011-12-02 13:24 | Equipment | Connector/jumper/splice/elbow/rack | 0 | WPT | 0 | 0
448 | 2012-04-26 04:26 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2012-06-03 07:50 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2012-06-06 07:36 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2012-06-19 18:59 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2012-07-04 22:41 | Undetermined | Undetermined | 1 | WPT | 0 | 0
448 | 2012-08-03 21:51 | Equipment | Conductor failure/wire down | 0 | WPT | 0 | 0
448 | 2012-08-13 16:51 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2012-09-29 11:20 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2012-10-23 10:34 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2013-01-05 23:01 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2013-06-28 16:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 0 | 0
448 | 2013-06-28 17:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 0 | 0
448 | 2013-09-02 14:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 0 | 0
448 | 2014-09-04 05:06 | Undetermined | Undetermined | 0 | WPT | 0 | 0
448 | 2014-11-12 10:43 | Undetermined | Undetermined | 0 | WPT | 0 | 0
449 | 2005-07-05 05:39 | Undetermined | Undetermined | 1 | MOR | 0 | 0
449 | 2005-07-18 16:42 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2005-07-18 18:28 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2006-11-15 12:46 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2007-08-15 16:18 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2008-08-21 20:33 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2008-09-03 16:36 | Equipment | Conductor failure/wire down | 0 | MOR | 0 | 0
449 | 2008-10-14 04:52 | Undetermined | Undetermined | 0 | MOR | 1 | 0
449 | 2009-02-10 06:59 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2009-11-07 02:57 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2009-11-30 09:06 | Equipment | Insulator/pin failure/wire floating | 0 | MOR | 0 | 0
449 | 2009-12-07 14:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MOR | 0 | 0
449 | 2009-12-13 06:48 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2010-01-19 16:16 | Equipment | Cutout failure | 0 | MOR | 0 | 0
449 | 2011-08-27 10:13 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2011-10-12 16:22 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2013-05-25 16:18 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2013-07-01 07:54 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2014-04-30 10:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MOR | 1 | 0
449 | 2014-08-17 16:59 | Undetermined | Undetermined | 0 | MOR | 0 | 0
449 | 2015-02-26 06:25 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MOR | 0 | 0
450 | 2006-06-14 08:55 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2007-02-08 11:44 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2008-04-15 20:18 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2008-07-13 20:05 | Undetermined | Undetermined | 1 | ESC | 0 | 0
450 | 2010-01-21 12:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ESC | 0 | 0
450 | 2010-12-23 13:22 | Equipment | Cutout failure | 0 | ESC | 0 | 0
450 | 2011-08-28 15:55 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2011-12-13 02:32 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2013-05-10 13:25 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2014-04-26 07:28 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2014-08-17 17:40 | Undetermined | Undetermined | 0 | ESC | 0 | 0
450 | 2014-09-07 13:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ESC | 0 | 0
470 | 2005-12-02 05:28 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2006-03-10 20:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2006-10-26 11:00 | Undetermined | Undetermined | 0 | HVW | 1 | 0
470 | 2006-10-26 13:50 | Undetermined | Undetermined | 0 | HVW | 1 | 0
470 | 2007-03-03 10:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 1 | 0
470 | 2007-03-03 16:34 | Weather | Wind - wires slap/pole down | 0 | HVW | 1 | 0
470 | 2007-03-16 17:52 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2007-11-16 11:59 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2008-12-15 10:01 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2009-09-23 17:51 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2010-01-18 13:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2010-01-21 07:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2010-02-27 10:08 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2011-02-18 22:36 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2011-03-20 15:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2011-03-20 17:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2011-03-20 18:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2011-07-04 07:31 | Undetermined | Undetermined | 1 | HVW | 0 | 0
470 | 2012-01-02 06:55 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2013-10-08 01:54 | Equipment | Crossarm failure | 0 | HVW | 0 | 0
470 | 2014-02-19 18:48 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2014-05-13 12:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 0 | 0
470 | 2014-05-14 09:47 | Undetermined | Undetermined | 0 | HVW | 0 | 0
470 | 2015-01-25 10:15 | Undetermined | Undetermined | 0 | HVW | 1 | 0
48 | 2008-02-02 13:20 | Equipment | Insulator/pin failure/wire floating | 0 | KSAN | 0 | 0
500 | 2013-05-02 16:06 | Equipment | Pole broke/rotted/on fire | 0 | MPE | 0 | 0
520 | 2005-02-23 04:37 | Weather | Wind - wires slap/pole down | 0 | DLZ | 0 | 0
520 | 2005-05-07 22:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
520 | 2005-07-21 06:49 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2005-08-02 08:17 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2006-02-15 14:55 | Equipment | Crossarm failure | 0 | DLZ | 0 | 0
520 | 2006-07-04 08:32 | Undetermined | Undetermined | 1 | DLZ | 0 | 0
520 | 2007-01-05 11:42 | Undetermined | Undetermined | 0 | DLZ | 1 | 0
520 | 2007-03-29 06:45 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2007-06-07 05:38 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2007-08-30 11:32 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2007-10-21 11:16 | Weather | Wind - wires slap/pole down | 0 | DLZ | 1 | 0
520 | 2008-01-05 07:30 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2008-05-22 19:51 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2008-07-10 09:18 | Undetermined | Undetermined | 1 | DLZ | 0 | 0
520 | 2009-06-25 08:01 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
520 | 2009-07-21 14:55 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2009-08-06 09:18 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2010-01-21 21:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2010-05-25 07:56 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2010-06-17 16:34 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2010-09-30 10:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2010-10-19 09:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2010-10-19 09:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2010-10-19 16:04 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2010-11-02 10:13 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2011-02-04 12:49 | Equipment | Crossarm failure | 0 | DLZ | 0 | 0
520 | 2011-03-12 00:03 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2011-05-19 13:12 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2011-09-26 07:21 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2012-03-18 18:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2012-04-04 10:57 | Equipment | Conductor failure/wire down | 0 | DLZ | 0 | 0
520 | 2012-04-22 05:07 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
520 | 2012-06-09 07:41 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2012-08-25 20:05 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
520 | 2012-09-14 15:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DLZ | 0 | 0
520 | 2012-09-15 16:14 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
520 | 2013-04-02 10:07 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2013-05-02 17:29 | Equipment | Pole broke/rotted/on fire | 0 | DLZ | 0 | 0
520 | 2013-06-11 05:35 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2013-09-05 22:34 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-01-06 10:35 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-03-19 09:24 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-04-01 08:03 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-04-13 09:32 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-04-16 16:31 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-05-10 17:11 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-06-27 09:51 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
520 | 2014-07-22 09:25 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2014-08-20 05:31 | Undetermined | Undetermined | 0 | DLZ | 0 | 0
520 | 2015-03-02 12:32 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DLZ | 0 | 0
521 | 2005-01-07 16:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV | 0 | 0
521 | 2005-02-19 09:12 | Weather | Wind - wires slap/pole down | 0 | RBV | 0 | 0
521 | 2005-06-18 17:49 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2005-09-21 11:19 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2005-12-24 13:18 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2006-03-20 10:51 | Equipment | Cutout failure | 0 | RBV | 0 | 0
521 | 2006-05-06 18:44 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2006-09-29 10:22 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2007-03-05 07:28 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2007-06-17 11:07 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2008-02-03 19:34 | Weather | Wind - wires slap/pole down | 0 | RBV | 0 | 0
521 | 2008-06-07 13:26 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2008-08-22 09:28 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2008-11-04 17:27 | Equipment | Cutout failure | 0 | RBV | 0 | 0
521 | 2009-01-27 20:24 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBV | 0 | 0
521 | 2009-06-03 19:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV | 0 | 0
521 | 2009-10-13 07:35 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2009-10-23 12:58 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2009-12-29 15:18 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2010-04-28 18:10 | Weather | Wind - wires slap/pole down | 0 | RBV | 0 | 0
521 | 2010-10-19 16:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV | 0 | 0
521 | 2011-03-16 11:48 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2011-03-17 14:08 | Equipment | Conductor failure/wire down | 0 | RBV | 0 | 0
521 | 2011-09-19 11:19 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2011-11-20 11:47 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2012-01-07 03:35 | Equipment | Insulator/pin failure/wire floating | 0 | RBV | 0 | 0
521 | 2012-06-16 12:28 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2012-08-15 10:57 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2012-10-12 00:18 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2013-06-04 22:34 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2014-07-24 17:14 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2014-09-14 14:54 | Undetermined | Undetermined | 0 | RBV | 0 | 0
521 | 2014-09-16 16:13 | Equipment | Pole broke/rotted/on fire | 0 | RBV | 0 | 0
521 | 2014-12-03 09:27 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RBV | 0 | 0
521 | 2015-02-09 21:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RBV | 0 | 0
521 | 2015-03-15 07:42 | Undetermined | Undetermined | 0 | RBV | 0 | 0
524 | 2005-02-11 09:48 | Weather | Wind - wires slap/pole down | 0 | LSV | 0 | 0
524 | 2005-02-25 17:44 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2005-08-02 20:44 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2006-01-25 07:04 | Weather | Wind - wires slap/pole down | 0 | LSV | 0 | 0
524 | 2006-02-21 01:47 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2006-06-02 05:30 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2007-03-09 18:12 | Equipment | Crossarm failure | 0 | LSV | 0 | 0
524 | 2007-04-01 07:09 | Equipment | Crossarm failure | 0 | LSV | 0 | 0
524 | 2007-10-21 19:40 | Weather | Wind - wires slap/pole down | 0 | LSV | 1 | 0
524 | 2007-10-22 06:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 1 | 0
524 | 2007-10-22 12:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 1 | 0
524 | 2007-10-29 17:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 0 | 0
524 | 2007-12-01 01:24 | Equipment | Conductor failure/wire down | 0 | LSV | 0 | 0
524 | 2008-01-03 08:19 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2008-05-30 03:16 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2008-06-18 04:30 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2008-07-14 16:08 | Undetermined | Undetermined | 1 | LSV | 0 | 0
524 | 2008-11-14 16:00 | Equipment | Pole broke/rotted/on fire | 0 | LSV | 0 | 0
524 | 2009-01-14 07:17 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2009-02-15 08:26 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2009-05-29 07:08 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2009-12-07 14:37 | Weather | Wind - wires slap/pole down | 0 | LSV | 0 | 0
524 | 2010-01-18 23:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 0 | 0
524 | 2010-01-19 18:53 | Weather | Wind - wires slap/pole down | 0 | LSV | 0 | 0
524 | 2010-01-21 06:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 0 | 0
524 | 2010-01-22 01:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 0 | 0
524 | 2010-02-01 21:30 | Equipment | Pole broke/rotted/on fire | 0 | LSV | 0 | 0
524 | 2010-02-08 07:52 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2010-09-30 13:01 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 0 | 0
524 | 2010-10-06 18:50 | Equipment | Connector/jumper/splice/elbow/rack | 0 | LSV | 0 | 0
524 | 2010-10-19 21:35 | Weather | Wind - wires slap/pole down | 0 | LSV | 0 | 0
524 | 2011-04-01 13:49 | Equipment | Crossarm failure | 0 | LSV | 0 | 0
524 | 2011-06-18 17:44 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2011-10-12 12:55 | Equipment | Conductor failure/wire down | 0 | LSV | 0 | 0
524 | 2012-02-06 10:31 | Equipment | Cutout failure | 0 | LSV | 0 | 0
524 | 2012-04-10 07:37 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2012-07-30 19:20 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2013-09-14 18:37 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2013-10-30 06:42 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2014-07-26 13:40 | Equipment | Pole broke/rotted/on fire | 0 | LSV | 0 | 0
524 | 2014-07-31 14:59 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2014-09-17 21:47 | Undetermined | Undetermined | 0 | LSV | 0 | 0
524 | 2014-12-03 02:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 0 | 0
524 | 2015-02-19 10:18 | Undetermined | Undetermined | 0 | LSV | 0 | 0
67 | 2005-07-06 04:52 | Undetermined | Undetermined | 1 | DHV | 0 | 0
67 | 2006-01-02 06:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DHV | 0 | 0
67 | 2006-04-26 02:59 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2006-12-24 08:24 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2007-01-12 00:10 | Equipment | Insulator/pin failure/wire floating | 0 | DHV | 0 | 0
67 | 2007-09-03 22:36 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2008-12-15 14:40 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2009-12-07 17:14 | Weather | Wind - wires slap/pole down | 0 | DHV | 0 | 0
67 | 2010-01-19 14:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DHV | 0 | 0
67 | 2010-10-22 20:44 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2011-04-12 08:26 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2012-10-20 08:28 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2013-03-04 22:53 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2013-04-20 07:57 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2013-06-17 05:17 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2013-12-04 01:40 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2014-08-03 12:02 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2014-09-12 15:20 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2014-10-28 10:50 | Undetermined | Undetermined | 0 | DHV | 0 | 0
67 | 2014-11-02 02:29 | Undetermined | Undetermined | 0 | DHV | 0 | 0
701 | 2005-04-29 08:17 | Undetermined | Undetermined | 0 | MVN | 0 | 0
701 | 2007-10-07 09:42 | Undetermined | Undetermined | 0 | MVN | 0 | 0
701 | 2013-12-16 14:24 | Undetermined | Undetermined | 0 | MVN | 0 | 0
701 | 2014-09-16 17:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MVN | 0 | 0
728 | 2005-01-27 11:45 | Undetermined | Undetermined | 0 | DMH | 0 | 0
728 | 2005-02-05 00:40 | Undetermined | Undetermined | 0 | DMH | 0 | 0
728 | 2009-09-29 22:48 | Equipment | Conductor failure/wire down | 0 | DMH | 0 | 0
73 | 2005-05-05 10:32 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2005-06-22 00:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DEN | 0 | 0
73 | 2005-07-13 07:06 | Equipment | Crossarm failure | 1 | DEN | 0 | 0
73 | 2007-01-01 11:21 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2007-04-29 06:00 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2007-10-22 04:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
73 | 2008-02-19 07:09 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2008-06-25 10:40 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2008-10-11 05:28 | Equipment | Cutout failure | 0 | DEN | 0 | 0
73 | 2009-12-07 17:21 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
73 | 2010-09-30 10:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
73 | 2011-11-02 08:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
73 | 2012-08-11 15:42 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2012-09-06 16:40 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2013-09-04 16:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
73 | 2013-09-04 17:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
73 | 2013-11-16 12:01 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2014-03-02 23:12 | Undetermined | Undetermined | 0 | DEN | 0 | 0
73 | 2014-04-30 06:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
73 | 2014-12-03 08:33 | Undetermined | Undetermined | 0 | DEN | 0 | 0
75 | 2005-01-04 10:13 | Equipment | Conductor failure/wire down | 0 | OTY | 0 | 0
75 | 2005-01-11 09:19 | Weather | Wind - wires slap/pole down | 0 | OTY | 0 | 0
75 | 2005-01-16 15:47 | Equipment | Conductor failure/wire down | 0 | OTY | 0 | 0
75 | 2005-01-17 11:03 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2005-02-11 01:54 | Equipment | Guy wire failure | 0 | OTY | 0 | 0
75 | 2005-04-21 18:36 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2005-10-29 13:25 | Equipment | Connector/jumper/splice/elbow/rack | 0 | OTY | 0 | 0
75 | 2006-01-02 14:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2006-01-07 07:07 | Equipment | Conductor failure/wire down | 0 | OTY | 0 | 0
75 | 2006-02-28 02:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2006-11-30 00:45 | Weather | Wind - wires slap/pole down | 0 | OTY | 1 | 0
75 | 2007-03-03 10:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0
75 | 2007-09-22 14:33 | Equipment | Connector/jumper/splice/elbow/rack | 0 | OTY | 0 | 0
75 | 2007-10-09 11:35 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2007-10-22 07:11 | Weather | Wind - wires slap/pole down | 0 | OTY | 1 | 0
75 | 2007-10-25 15:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2007-10-26 17:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2007-11-19 10:58 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2007-11-30 09:24 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2007-12-23 17:20 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2008-01-07 00:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2008-01-07 00:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 1
75 | 2008-01-07 07:25 | Weather | Wind - wires slap/pole down | 0 | OTY | 0 | 0
75 | 2008-06-26 22:47 | Equipment | Conductor failure/wire down | 0 | OTY | 0 | 0
75 | 2008-06-27 08:54 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2008-11-09 12:17 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2008-11-16 13:02 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2008-12-09 12:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0
75 | 2008-12-09 12:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0
75 | 2008-12-09 14:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0
75 | 2009-01-29 15:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2009-02-09 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2009-02-24 08:05 | Equipment | Connector/jumper/splice/elbow/rack | 0 | OTY | 0 | 0
75 | 2009-04-03 10:08 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2009-04-05 09:30 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2009-10-06 12:27 | Weather | Wind - wires slap/pole down | 0 | OTY | 0 | 0
75 | 2009-11-22 07:09 | Equipment | Conductor failure/wire down | 0 | OTY | 0 | 0
75 | 2009-12-07 16:30 | Weather | Wind - wires slap/pole down | 0 | OTY | 0 | 0
75 | 2009-12-09 14:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2010-01-19 14:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2010-01-20 10:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2010-01-20 11:10 | Equipment | Insulator/pin failure/wire floating | 0 | OTY | 0 | 0
75 | 2010-01-21 20:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2010-01-22 08:02 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2010-07-14 17:25 | Equipment | Conductor contact/wire slap | 1 | OTY | 0 | 0
75 | 2010-09-03 21:21 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2010-09-30 19:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2011-02-02 14:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0
75 | 2011-08-26 14:52 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2011-10-05 22:39 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
75 | 2011-12-06 08:41 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2012-05-25 11:52 | Equipment | Crossarm failure | 0 | OTY | 0 | 0
75 | 2013-07-26 18:50 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2014-05-01 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0
75 | 2014-05-13 08:37 | Weather | Wind - wires slap/pole down | 0 | OTY | 0 | 0
75 | 2014-05-14 08:56 | Undetermined | Undetermined | 0 | OTY | 0 | 0
75 | 2014-08-30 16:17 | Undetermined | Undetermined | 0 | OTY | 0 | 0
78 | 2006-11-30 07:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VJS | 1 | 0
78 | 2007-11-02 18:33 | Undetermined | Undetermined | 0 | VJS | 0 | 0
78 | 2009-09-02 11:48 | Undetermined | Undetermined | 0 | VJS | 0 | 0
78 | 2012-03-18 09:46 | Weather | Wind - wires slap/pole down | 0 | VJS | 0 | 0
78 | 2013-03-26 00:11 | Undetermined | Undetermined | 0 | VJS | 0 | 0
78 | 2014-04-30 06:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VJS | 1 | 0
79 | 2005-01-03 16:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2005-03-19 01:39 | Equipment | Pole broke/rotted/on fire | 0 | DEN | 0 | 0
79 | 2005-03-19 08:03 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2005-03-31 10:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2005-03-31 15:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2005-04-22 17:08 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2005-04-24 07:42 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2005-06-02 04:10 | Equipment | Crossarm failure | 0 | DEN | 0 | 0
79 | 2005-06-02 23:41 | Equipment | Crossarm failure | 0 | DEN | 0 | 0
79 | 2005-06-04 04:57 | Equipment | Crossarm failure | 0 | DEN | 0 | 0
79 | 2005-06-06 06:31 | Equipment | Crossarm failure | 0 | DEN | 0 | 0
79 | 2005-06-06 12:02 | Equipment | Crossarm failure | 0 | DEN | 0 | 0
79 | 2005-09-19 08:05 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2005-09-27 20:50 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2006-04-24 16:54 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2006-04-29 19:33 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2006-11-29 22:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2007-01-29 06:24 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2007-06-19 06:23 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2007-08-26 10:37 | Equipment | Hardware failure | 0 | DEN | 0 | 0
79 | 2007-10-21 22:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2007-10-23 13:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2007-10-23 19:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2008-03-02 00:50 | Equipment | Crossarm failure | 0 | DEN | 0 | 0
79 | 2008-03-03 03:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2008-03-03 06:16 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2008-03-18 15:22 | Equipment | Conductor failure/wire down | 0 | DEN | 0 | 0
79 | 2008-07-10 08:31 | Undetermined | Undetermined | 1 | DEN | 0 | 0
79 | 2009-01-10 05:19 | Weather | Wind - wires slap/pole down | 0 | DEN | 1 | 0
79 | 2009-01-10 21:56 | Equipment | Insulator/pin failure/wire floating | 0 | DEN | 1 | 0
79 | 2009-01-11 00:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2009-01-11 01:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2009-01-11 11:18 | Weather | Wind - wires slap/pole down | 0 | DEN | 1 | 0
79 | 2009-02-11 06:55 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DEN | 0 | 0
79 | 2009-09-02 15:29 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2009-11-28 12:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2009-12-07 21:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2009-12-08 10:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2010-01-23 11:09 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2010-03-16 18:21 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2010-04-23 10:41 | Equipment | Conductor failure/wire down | 0 | DEN | 0 | 0
79 | 2010-08-15 23:53 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2010-08-30 12:23 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2010-09-30 10:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2010-11-08 01:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | DEN | 0 | 0
79 | 2010-11-13 03:47 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2010-11-28 12:23 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2011-01-14 20:25 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2011-01-23 08:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2011-02-03 13:31 | Undetermined | Undetermined | 0 | DEN | 1 | 0
79 | 2011-02-26 13:55 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2011-03-07 10:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2011-03-07 18:07 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2011-03-07 21:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2011-05-18 06:35 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2011-07-06 13:04 | Equipment | Crossarm failure | 1 | DEN | 0 | 0
79 | 2011-07-11 17:15 | Equipment | Crossarm failure | 1 | DEN | 0 | 0
79 | 2011-07-24 19:14 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2011-09-13 23:26 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-01-21 07:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2012-01-23 11:05 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-02-28 18:52 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-03-21 15:22 | Equipment | Pole broke/rotted/on fire | 0 | DEN | 0 | 0
79 | 2012-03-22 12:39 | Equipment | Insulator/pin failure/wire floating | 0 | DEN | 0 | 0
79 | 2012-03-25 17:45 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2012-03-26 05:23 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-04-01 14:00 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-04-14 07:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2012-08-08 13:43 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-08-13 13:24 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-08-15 13:38 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-10-04 09:26 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-10-06 16:13 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2012-12-13 13:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2013-01-26 07:00 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2013-02-08 16:07 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2013-02-16 00:54 | Equipment | Insulator/pin failure/wire floating | 0 | DEN | 0 | 0
79 | 2013-02-20 03:22 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2013-04-05 04:58 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2013-07-06 09:35 | Undetermined | Undetermined | 1 | DEN | 0 | 0
79 | 2013-07-21 19:44 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2013-08-04 15:28 | Equipment | Conductor failure/wire down | 0 | DEN | 0 | 0
79 | 2014-01-15 08:24 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2014-02-13 02:53 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2014-03-26 18:10 | Equipment | Conductor failure/wire down | 0 | DEN | 0 | 0
79 | 2014-03-30 08:10 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2014-04-28 19:30 | Equipment | Conductor contact/wire slap | 0 | DEN | 0 | 0
79 | 2014-04-30 06:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0
79 | 2014-05-01 03:15 | Weather | Wind - wires slap/pole down | 0 | DEN | 1 | 0
79 | 2014-05-13 09:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2014-05-13 13:56 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2014-05-14 06:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 0 | 0
79 | 2014-07-29 06:43 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2014-08-21 17:49 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2014-10-18 10:01 | Undetermined | Undetermined | 0 | DEN | 0 | 0
79 | 2014-11-05 20:38 | Weather | Wind - wires slap/pole down | 0 | DEN | 0 | 0
79 | 2015-01-01 23:58 | Equipment | Conductor failure/wire down | 0 | DEN | 0 | 0
79 | 2015-01-24 07:44 | Equipment | Conductor contact/wire slap | 0 | DEN | 1 | 0
907 | 2005-04-29 10:43 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2005-05-19 06:56 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC | 0 | 0
907 | 2005-12-07 12:56 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2006-03-29 09:45 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2006-03-29 18:31 | Equipment | Conductor failure/wire down | 0 | VLC | 0 | 0
907 | 2006-04-23 07:46 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2006-08-28 11:53 | Equipment | Conductor failure/wire down | 0 | VLC | 0 | 0
907 | 2007-12-27 22:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC | 0 | 0
907 | 2008-01-21 11:37 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2008-05-23 15:51 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2010-09-30 12:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 0 | 0
907 | 2011-10-07 09:48 | Undetermined | Undetermined | 0 | VLC | 0 | 0
907 | 2014-08-23 01:23 | Undetermined | Undetermined | 0 | VLC | 0 | 0
908 | 2005-02-10 21:40 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2005-04-01 04:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 1 | 0
908 | 2005-07-23 04:53 | Weather | Wind - wires slap/pole down | 0 | HID | 0 | 0
908 | 2005-12-21 15:09 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2006-01-02 09:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 0
908 | 2006-01-25 11:27 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2006-05-16 07:06 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2006-07-10 18:43 | Undetermined | Undetermined | 1 | HID | 0 | 0
908 | 2006-10-13 10:28 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2006-12-03 08:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 1 | 0
908 | 2007-01-30 07:14 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2007-04-04 17:39 | Equipment | Cutout failure | 0 | HID | 0 | 0
908 | 2007-07-26 09:18 | Equipment | Crossarm failure | 0 | HID | 0 | 0
908 | 2007-10-22 04:18 | Undetermined | Undetermined | 0 | HID | 1 | 0
908 | 2007-12-18 16:19 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2007-12-26 22:03 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2008-01-08 09:11 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2008-01-16 18:58 | Weather | Wind - wires slap/pole down | 0 | HID | 0 | 0
908 | 2008-01-25 13:26 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2008-02-05 07:02 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HID | 0 | 0
908 | 2008-02-17 10:10 | Equipment | Conductor failure/wire down | 0 | HID | 0 | 0
908 | 2008-03-24 14:10 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2008-05-22 20:31 | Equipment | Cutout failure | 0 | HID | 0 | 0
908 | 2008-06-18 19:19 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2008-06-21 23:07 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2009-05-21 19:00 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2009-07-27 13:47 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2009-12-06 02:12 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2009-12-23 02:13 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HID | 0 | 0
908 | 2010-01-20 17:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 0
908 | 2010-10-19 02:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 0
908 | 2010-10-19 02:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 1
908 | 2010-12-22 04:11 | Weather | Wind - wires slap/pole down | 0 | HID | 0 | 0
908 | 2011-04-25 07:09 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2012-01-09 16:46 | Equipment | Insulator/pin failure/wire floating | 0 | HID | 0 | 0
908 | 2012-05-13 12:57 | Equipment | Cutout failure | 0 | HID | 0 | 0
908 | 2012-06-01 16:41 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2013-04-22 06:28 | Equipment | Conductor failure/wire down | 0 | HID | 0 | 0
908 | 2013-10-10 03:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 0
908 | 2014-07-02 15:40 | Undetermined | Undetermined | 1 | HID | 0 | 0
908 | 2014-10-23 10:03 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2014-12-12 12:46 | Undetermined | Undetermined | 0 | HID | 0 | 0
908 | 2015-02-24 06:47 | Equipment | Cutout failure | 0 | HID | 0 | 0
909 | 2005-01-22 07:20 | Undetermined | Undetermined | 0 | VLC | 0 | 0
909 | 2006-03-01 10:02 | Equipment | Cutout failure | 0 | VLC | 0 | 0
909 | 2006-03-29 16:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 0 | 0
909 | 2006-06-06 05:41 | Undetermined | Undetermined | 0 | VLC | 0 | 0
909 | 2006-10-31 10:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC | 0 | 0
909 | 2006-12-10 14:49 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 0 | 0
909 | 2007-03-03 13:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0
909 | 2007-10-22 12:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0
909 | 2007-10-23 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0
909 | 2007-10-23 16:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0
909 | 2007-12-05 08:12 | Undetermined | Undetermined | 0 | VLC | 0 | 0
909 | 2007-12-31 20:21 | Weather | Wind - wires slap/pole down | 0 | VLC | 0 | 0
909 | 2008-01-01 08:46 | Weather | Wind - wires slap/pole down | 0 | VLC | 1 | 0
909 | 2009-10-29 22:56 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC | 0 | 0
909 | 2010-01-21 15:49 | Weather | Wind - wires slap/pole down | 0 | VLC | 0 | 0
909 | 2010-04-15 13:04 | Equipment | Conductor contact/wire slap | 0 | VLC | 0 | 0
909 | 2010-05-28 16:44 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VLC | 0 | 0
909 | 2011-01-23 08:11 | Weather | Wind - wires slap/pole down | 0 | VLC | 1 | 0
909 | 2011-05-28 17:34 | Undetermined | Undetermined | 0 | VLC | 0 | 0
909 | 2011-08-04 14:43 | Undetermined | Undetermined | 0 | VLC | 0 | 0
909 | 2012-09-10 19:18 | Equipment | Pole broke/rotted/on fire | 0 | VLC | 0 | 0
909 | 2014-03-09 12:43 | Equipment | Insulator/pin failure/wire floating | 0 | VLC | 1 | 0
909 | 2014-05-14 08:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 0 | 0
92 | 2007-08-25 09:48 | Undetermined | Undetermined | 0 | OTY | 0 | 0
92 | 2010-01-19 13:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 0
920 | 2005-05-15 00:29 | Undetermined | Undetermined | 0 | SYC | 0 | 0
920 | 2006-03-10 22:47 | Weather | Wind - wires slap/pole down | 0 | SYC | 0 | 0
920 | 2006-04-11 15:23 | Undetermined | Undetermined | 0 | SYC | 0 | 0
920 | 2006-04-13 13:24 | Undetermined | Undetermined | 0 | SYC | 0 | 0
920 | 2006-09-01 13:13 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SYC | 0 | 0
920 | 2006-09-20 07:57 | Undetermined | Undetermined | 0 | SYC | 0 | 0
920 | 2009-05-14 00:06 | Undetermined | Undetermined | 0 | SYC | 0 | 0
920 | 2010-09-30 17:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SYC | 0 | 0
920 | 2012-03-26 06:46 | Undetermined | Undetermined | 0 | SYC | 0 | 0
970 | 2006-02-12 12:26 | Undetermined | Undetermined | 0 | RAM | 0 | 0
970 | 2007-05-06 03:21 | Undetermined | Undetermined | 0 | RAM | 0 | 0
970 | 2010-04-06 09:12 | Undetermined | Undetermined | 0 | RAM | 0 | 0
971 | 2005-07-30 21:12 | Equipment | Crossarm failure | 0 | MGR | 0 | 0
971 | 2005-10-19 11:38 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2005-11-04 19:21 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2006-11-01 12:27 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2008-01-06 01:31 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2008-01-07 07:38 | Weather | Wind - wires slap/pole down | 0 | MGR | 0 | 0
971 | 2008-09-12 08:54 | Equipment | Crossarm failure | 0 | MGR | 0 | 0
971 | 2009-02-09 12:50 | Weather | Wind - wires slap/pole down | 0 | MGR | 0 | 0
971 | 2009-03-16 10:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR | 0 | 0
971 | 2009-09-06 08:30 | Equipment | Conductor failure/wire down | 0 | MGR | 0 | 0
971 | 2010-01-19 17:40 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGR | 0 | 0
971 | 2010-03-12 06:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR | 0 | 0
971 | 2010-09-30 12:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGR | 0 | 0
971 | 2011-03-22 10:20 | Equipment | Crossarm failure | 0 | MGR | 0 | 0
971 | 2011-05-29 03:38 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2012-02-04 14:58 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2012-03-13 23:51 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR | 0 | 0
971 | 2012-10-06 15:07 | Undetermined | Undetermined | 0 | MGR | 0 | 0
971 | 2012-12-23 16:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MGR | 0 | 0
971 | 2014-02-18 17:01 | Equipment | Connector/jumper/splice/elbow/rack | 0 | MGR | 0 | 0
971 | 2014-08-31 17:15 | Undetermined | Undetermined | 0 | MGR | 0 | 0
972 | 2005-01-02 14:33 | Equipment | Conductor failure/wire down | 0 | HVY | 0 | 0
972 | 2005-01-10 07:48 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2006-01-23 08:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 1 | 0
972 | 2006-09-03 13:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2007-03-04 07:35 | Undetermined | Undetermined | 0 | HVY | 1 | 0
972 | 2007-04-24 14:23 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 0 | 0
972 | 2007-06-16 18:25 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2007-10-21 20:27 | Weather | Wind - wires slap/pole down | 0 | HVY | 1 | 0
972 | 2007-10-22 06:31 | Weather | Wind - wires slap/pole down | 0 | HVY | 1 | 0
972 | 2007-10-22 18:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 1 | 0
972 | 2007-11-05 09:00 | Equipment | Pole broke/rotted/on fire | 0 | HVY | 0 | 0
972 | 2008-01-05 07:12 | Equipment | Cutout failure | 0 | HVY | 0 | 0
972 | 2008-02-23 11:49 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2008-08-29 20:18 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2008-09-01 21:56 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2008-12-25 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2009-05-20 06:44 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 0 | 0
972 | 2009-11-28 08:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2009-12-07 14:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2009-12-22 08:22 | Equipment | Insulator/pin failure/wire floating | 0 | HVY | 0 | 0
972 | 2010-01-19 19:56 | Weather | Wind - wires slap/pole down | 0 | HVY | 0 | 0
972 | 2010-01-21 17:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2010-04-07 09:41 | Equipment | Insulator/pin failure/wire floating | 0 | HVY | 0 | 0
972 | 2011-05-01 14:34 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2011-08-05 05:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 0 | 0
972 | 2011-11-30 21:41 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2011-12-12 14:21 | Weather | Wind - wires slap/pole down | 0 | HVY | 0 | 0
972 | 2012-01-24 05:12 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2012-03-08 03:25 | Equipment | Conductor failure/wire down | 0 | HVY | 0 | 0
972 | 2013-04-17 14:32 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 0 | 0
972 | 2013-04-30 08:20 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2013-08-09 11:10 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 0 | 0
972 | 2013-10-06 10:06 | Equipment | Cutout failure | 0 | HVY | 0 | 0
972 | 2013-10-10 00:19 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2014-02-28 12:42 | Weather | Wind - wires slap/pole down | 0 | HVY | 0 | 0
972 | 2014-04-30 11:13 | Undetermined | Undetermined | 0 | HVY | 1 | 0
972 | 2014-05-06 22:17 | Equipment | Crossarm failure | 0 | HVY | 0 | 0
972 | 2014-05-13 10:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2014-05-14 08:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 0 | 0
972 | 2014-07-06 11:31 | Undetermined | Undetermined | 1 | HVY | 0 | 0
972 | 2014-07-10 22:53 | Equipment | Insulator/pin failure/wire floating | 1 | HVY | 0 | 0
972 | 2014-08-29 04:43 | Undetermined | Undetermined | 0 | HVY | 0 | 0
972 | 2014-08-29 14:49 | Equipment | Conductor failure/wire down | 0 | HVY | 0 | 0
972 | 2015-01-24 12:00 | Undetermined | Undetermined | 0 | HVY | 1 | 0
972 | 2015-01-25 09:02 | Equipment | Conductor contact/wire slap | 0 | HVY | 1 | 0
973 | 2005-02-11 06:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2006-01-02 14:43 | Weather | Wind - wires slap/pole down | 0 | SPP | 0 | 0
973 | 2006-01-24 05:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2006-07-14 08:15 | Undetermined | Undetermined | 1 | SPP | 0 | 0
973 | 2006-08-07 12:25 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2007-04-20 15:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2007-08-30 17:02 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2007-10-13 10:35 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2009-03-07 13:45 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2009-04-09 16:47 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SPP | 0 | 0
973 | 2009-04-22 10:26 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2010-01-19 14:13 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2010-01-21 07:22 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2010-01-21 12:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2010-09-30 12:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2010-10-20 17:35 | Equipment | Connector/jumper/splice/elbow/rack | 0 | SPP | 0 | 0
973 | 2012-03-19 07:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2012-05-09 19:54 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2013-03-12 15:53 | Equipment | Crossarm failure | 0 | SPP | 0 | 0
973 | 2014-02-28 12:37 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2014-02-28 16:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
973 | 2014-04-26 09:21 | Undetermined | Undetermined | 0 | SPP | 0 | 0
973 | 2014-05-14 19:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SPP | 0 | 0
974 | 2005-02-03 19:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA | 0 | 0
974 | 2005-11-15 12:26 | Undetermined | Undetermined | 0 | BNA | 1 | 0
974 | 2006-12-27 07:25 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA | 0 | 0
974 | 2010-03-03 11:18 | Undetermined | Undetermined | 0 | BNA | 0 | 0
974 | 2010-10-08 10:06 | Undetermined | Undetermined | 0 | BNA | 0 | 0
974 | 2011-09-07 18:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA | 0 | 0
974 | 2012-03-18 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA | 0 | 0
974 | 2012-03-18 12:42 | Weather | Wind - wires slap/pole down | 0 | BNA | 0 | 0
974 | 2012-03-18 15:13 | Weather | Wind - wires slap/pole down | 0 | BNA | 0 | 0
974 | 2012-03-19 07:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BNA | 0 | 0
974 | 2012-10-31 17:32 | Undetermined | Undetermined | 0 | BNA | 0 | 0
974 | 2014-10-11 03:52 | Equipment | Conductor contact/wire slap | 0 | BNA | 0 | 0
974 | 2015-01-25 10:25 | Undetermined | Undetermined | 0 | BNA | 1 | 0
974 | 2015-01-25 10:32 | Undetermined | Undetermined | 0 | BNA | 1 | 1
974 | 2015-01-25 10:51 | Undetermined | Undetermined | 0 | BNA | 1 | 1
984 | 2005-03-01 10:04 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2005-07-08 13:42 | Equipment | Pole broke/rotted/on fire | 1 | CAP | 0 | 0
984 | 2006-01-03 09:00 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2006-02-22 10:33 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2006-03-16 18:20 | Equipment | Conductor failure/wire down | 0 | CAP | 0 | 0
984 | 2006-04-20 10:30 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2006-04-22 07:19 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2006-11-20 01:38 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2007-01-21 16:04 | Equipment | Connector/jumper/splice/elbow/rack | 0 | CAP | 0 | 0
984 | 2007-02-24 13:09 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2007-05-12 11:21 | Undetermined | Undetermined | 0 | CAP | 0 | 0
984 | 2007-11-28 13:17 | Equipment | Conductor failure/wire down | 0 | CAP | 0 | 0
984 | 2010-01-06 10:18 | Equipment | Pole broke/rotted/on fire | 0 | CAP | 0 | 0
984 | 2011-09-29 05:26 | Undetermined | Undetermined | 0 | CAP | 0 | 0
CTL1 | 2008-09-08 07:07 | Undetermined | Undetermined | 0 | PAM | 0 | 0
RB1 | 2007-07-02 14:30 | Undetermined | Undetermined | 1 | RNB | 0 | 0
RB1 | 2007-07-02 14:30 | Undetermined | Undetermined | 1 | RNB | 0 | 1
RB1 | 2009-12-02 06:29 | Equipment | Conductor failure/wire down | 0 | RNB | 0 | 0
RB1 | 2009-12-02 06:29 | Equipment | Conductor failure/wire down | 0 | RNB | 0 | 1
RB1 | 2011-07-05 02:29 | Undetermined | Undetermined | 1 | RNB | 0 | 0
RB1 | 2011-07-05 02:29 | Undetermined | Undetermined | 1 | RNB | 0 | 1
RB1 | 2011-09-08 13:10 | Undetermined | Undetermined | 0 | RNB | 0 | 0
RB1 | 2011-09-08 13:10 | Undetermined | Undetermined | 0 | RNB | 0 | 1
RB1 | 2013-02-01 05:39 | Equipment | Conductor contact/wire slap | 0 | RNB | 0 | 0
RB1 | 2013-02-01 05:39 | Equipment | Conductor contact/wire slap | 0 | RNB | 0 | 1
RB1 | 2013-02-01 07:13 | Equipment | Conductor contact/wire slap | 0 | RNB | 0 | 0
RB1 | 2013-02-01 07:13 | Equipment | Conductor contact/wire slap | 0 | RNB | 0 | 1
RB1 | 2013-06-28 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RNB | 0 | 0
RB1 | 2013-06-28 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RNB | 0 | 1
TM1 | 2005-05-07 21:39 | Undetermined | Undetermined | 0 | PTM | 0 | 0
TM1 | 2010-01-22 07:31 | Equipment | Circuit Breaker/Recloser Failure (Sub) | 0 | PTM | 0 | 0
TM1 | 2010-01-23 07:57 | Equipment | Circuit Breaker/Recloser Failure (Sub) | 0 | PTM | 0 | 0
TM1 | 2010-07-14 11:01 | Undetermined | Undetermined | 1 | PTM | 0 | 0
TM1 | 2010-07-15 09:57 | Undetermined | Undetermined | 1 | PTM | 0 | 0
TM1 | 2010-08-26 12:08 | Undetermined | Undetermined | 0 | PTM | 0 | 0
TM1 | 2011-11-21 18:26 | Undetermined | Undetermined | 0 | PTM | 0 | 0
TM1 | 2013-03-04 20:13 | Equipment | Cutout failure | 0 | PTM | 0 | 0
TM1 | 2013-03-23 11:16 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PTM | 0 | 0
TM1 | 2013-07-22 08:34 | Undetermined | Undetermined | 0 | PTM | 0 | 0
TM1 | 2013-08-10 11:00 | Undetermined | Undetermined | 0 | PTM | 0 | 0
TM1 | 2014-05-25 16:23 | Undetermined | Undetermined | 0 | PTM | 0 | 0

## FireWeatherOutages
Circuit | Occurrence | Cause Category | Cause Description | Control Date | Station Code | FireWeather | Reclose | Actv Station | Max48Gust
1021 | 2011-02-02 01:13 | Weather | Wind - wires slap/pole down | 0 | HID | 1 | 0 | HIDSD | 29 | 2005-01-01 | Bin | Frequency |  | Total | Excess Outgs | Err | Norm 2006 | NormErr
1030 | 2007-10-22 00:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC | 1 | 0 | VLCC1 | 52 | 2006-01-01 | 2006-01-01 | 11 | 2005-01-01 | 165 | 5.7127 | 3.3166 | 2.2848 | 1.3265
1030 | 2007-10-22 02:06 | Weather | Wind - wires slap/pole down | 0 | HHC | 1 | 0 | VLCC1 | 52 | 2007-01-01 | 2007-01-01 | 22 | 2006-01-01 | Backgrounds | 16.7127 | 4.6904 | 3.1609 | 0.8871
1030 | 2011-01-23 05:20 | Undetermined | Undetermined | 0 | HHC | 1 | 0 | VLCC1 | 29 | 2008-01-01 | 2008-01-01 | 62 | 2007-01-01 | 54.1953 | 56.7127 | 7.874 | 2.9721 | 0.41265
1030 | 2014-03-09 12:44 | Equipment | Insulator/pin failure/wire floating | 0 | HHC | 1 | 0 | HHCSD | 43 | 2009-01-01 | 2009-01-01 | 17 | 2008-01-01 | Bkd/Yr | 11.7127 | 4.1231 | 1.9243 | 0.67738
1101 | 2007-10-22 01:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB | 1 | 0 | KNKX | 27.68 | 2010-01-01 | 2010-01-01 | 10 | 2009-01-01 | 5.2873 | 4.7127 | 3.1623 | 1.3088 | 0.87826
1101 | 2007-10-22 02:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WRB | 1 | 0 | KNKX | 27.68 | 2011-01-01 | 2011-01-01 | 0 | 2010-01-01
1215 | 2007-01-06 03:45 | Weather | Wind - wires slap/pole down | 0 | CWD | 1 | 0 | CMNC1 | 32 | 2012-01-01 | 2012-01-01 | 13 | 2011-01-01 |  | 7.7127 | 3.6056 | 2.9048 | 1.358
1215 | 2007-10-22 09:17 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CWD | 1 | 0 | CMNC1 | 58 | 2013-01-01 | 2013-01-01 | 0 | 2012-01-01
1215 | 2014-04-30 07:45 | Weather | Wind - wires slap/pole down | 0 | CWD | 1 | 0 | CWDSD | 76 | 2014-01-01 | 2014-01-01 | 0 | 2013-01-01
1215 | 2014-05-01 06:55 | Equipment | Conductor contact/wire slap | 0 | CWD | 1 | 0 | CWDSD | 76 | 2015-01-01 | 2015-01-01 | 20 | 2014-01-01 |  | 14.7127 | 4.4721 | 2.3601 | 0.71738
1458 | 2007-10-22 11:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0 | ANEC1 | 59 | 2016-01-01 | 2016-01-01 | 10 | 2015-01-01 |  | 4.7127 | 3.1623 | 1.1994 | 0.80483
1458 | 2007-10-23 08:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0 | ANEC1 | 59 |  | More | 0
1458 | 2009-01-11 02:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0 | ANEC1 | 66
157 | 2005-03-31 13:21 | Weather | Circuit Flashover/fog/foreign object | 0 | BAJC1 | 1 | 0 | POTC1 | 44
157 | 2005-11-14 15:58 | Undetermined | Undetermined | 0 | BAJC1 | 1 | 0 | POTC1 | 33
157 | 2007-03-03 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 1 | 0 | POTC1 | 50
157 | 2007-10-21 09:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 1 | 0 | POTC1 | 69
157 | 2014-04-30 06:07 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BAJC1 | 1 | 0 | BAJC1 | 28
170 | 2007-01-05 11:43 | Equipment | Conductor failure/wire down | 0 | BRG | 1 | 0 | FHCC1 | 43
172 | 2008-12-05 16:25 | Undetermined | Undetermined | 0 | BRG | 1 | 0 | FHCC1 | 16
175 | 2008-01-01 07:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 1 | 0 | KRNM | 44.16
204 | 2005-11-14 08:54 | Undetermined | Undetermined | 0 | CAP | 1 | 0 | CAPC1 | 19
206 | 2007-10-22 04:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | CBD | 1 | 0 | KCRQ | 29.44
206 | 2008-12-09 14:40 | Equipment | Conductor failure/wire down | 0 | CBD | 1 | 0 | KCRQ | 14.72
210 | 2009-01-10 10:10 | Undetermined | Undetermined | 0 | COY | 1 | 0 | RCHC1 | 37
211 | 2005-11-18 18:05 | Undetermined | Undetermined | 0 | EWN | 1 | 0 | RCHC1 | 26
214 | 2007-03-04 08:50 | Undetermined | Undetermined | 0 | RIN | 1 | 0 | GOSC1 | 37
214 | 2014-04-30 09:14 | Undetermined | Undetermined | 0 | RIN | 1 | 0 | RINSD | 36
216 | 2005-04-01 10:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 1 | 0 | VLCC1 | 41
216 | 2006-02-05 11:04 | Undetermined | Undetermined | 0 | RIN | 1 | 0 | VLCC1 | 41
216 | 2006-02-08 12:21 | Undetermined | Undetermined | 0 | RIN | 1 | 0 | VLCC1 | 27
216 | 2007-03-04 09:31 | Undetermined | Undetermined | 0 | RIN | 1 | 0 | GOSC1 | 37
217 | 2006-01-23 19:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 1 | 0 | VLCC1 | 33
217 | 2011-01-23 06:44 | Equipment | Conductor failure/wire down | 0 | PAU | 1 | 0 | PAUSD | 32
217 | 2014-04-30 08:11 | Undetermined | Undetermined | 0 | PAU | 1 | 0 | PAUSD | 33
217 | 2014-04-30 11:21 | Equipment | Conductor failure/wire down | 0 | PAU | 1 | 0 | PAUSD | 33
217 | 2015-01-24 04:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PAU | 1 | 0 | PAUSD | 33
217 | 2015-01-24 07:04 | Equipment | Conductor contact/wire slap | 0 | PAU | 1 | 0 | PAUSD | 33
217 | 2015-01-24 09:26 | Undetermined | Undetermined | 0 | PAU | 1 | 0 | PAUSD | 33
217 | 2015-01-24 14:23 | Equipment | Conductor contact/wire slap | 0 | PAU | 1 | 0 | PAUSD | 33
220 | 2006-11-30 06:19 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0 | PIHC1 | 36
220 | 2007-10-22 05:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0 | PIHC1 | 56
220 | 2011-02-02 06:12 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0 | YSASD | 46
220 | 2014-11-25 03:41 | Undetermined | Undetermined | 0 | YSA | 1 | 0 | YSASD | 36
221 | 2005-04-01 11:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0 | PIHC1 | 42
221 | 2007-03-02 13:46 | Equipment | Cutout failure | 0 | YSA | 1 | 0 | PIHC1 | 37
221 | 2008-12-05 06:38 | Undetermined | Undetermined | 0 | YSA | 1 | 0 | PIHC1 | 27
222 | 2005-04-01 05:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0 | PIHC1 | 42
222 | 2006-11-30 04:49 | Undetermined | Undetermined | 0 | YSA | 1 | 0 | PIHC1 | 36
222 | 2006-11-30 10:41 | Undetermined | Undetermined | 0 | YSA | 1 | 0 | PIHC1 | 36
222 | 2006-12-03 09:45 | Equipment | Connector/jumper/splice/elbow/rack | 0 | YSA | 1 | 0 | PIHC1 | 31
222 | 2006-12-03 11:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0 | PIHC1 | 31
222 | 2007-01-06 02:15 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0 | PIHC1 | 33
222 | 2007-01-07 06:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0 | PIHC1 | 41
222 | 2007-01-07 08:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | YSA | 1 | 0 | PIHC1 | 41
222 | 2008-12-10 21:10 | Equipment | Cutout failure | 0 | YSA | 1 | 0 | PIHC1 | 27
222 | 2011-02-02 07:18 | Weather | Wind - wires slap/pole down | 0 | YSA | 1 | 0 | YSASD | 46
233 | 2009-01-10 20:26 | Undetermined | Undetermined | 0 | FBK | 1 | 0 | SRUC1 | 25
235 | 2007-10-22 08:05 | Weather | Wind - wires slap/pole down | 0 | RAM | 1 | 0 | GOSC1 | 55
236 | 2007-03-04 10:39 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RAM | 1 | 0 | GOSC1 | 37
236 | 2008-01-01 02:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0 | GOSC1 | 44
236 | 2008-01-01 03:43 | Equipment | Insulator/pin failure/wire floating | 0 | RAM | 1 | 0 | GOSC1 | 44
236 | 2008-01-01 05:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0 | GOSC1 | 44
236 | 2008-01-01 07:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0 | GOSC1 | 44
236 | 2014-04-30 10:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RAM | 1 | 0 | RAMSD | 38
237 | 2008-12-09 15:25 | Undetermined | Undetermined | 0 | GOS | 1 | 0 | GOSC1 | 31
237 | 2011-02-02 08:12 | Weather | Wind - wires slap/pole down | 0 | GOS | 1 | 0 | GOSSD | 49
239 | 2006-01-06 22:24 | Undetermined | Undetermined | 0 | FBK | 1 | 0 | SRUC1 | 34
239 | 2006-01-23 08:31 | Undetermined | Undetermined | 0 | FBK | 1 | 0 | SRUC1 | 35
239 | 2006-01-23 09:30 | Weather | Wind - wires slap/pole down | 0 | FBK | 1 | 0 | SRUC1 | 35
239 | 2006-02-06 17:43 | Undetermined | Undetermined | 0 | FBK | 1 | 0 | SRUC1 | 34
240 | 2011-01-23 07:51 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 1 | 0 | BVYSD | 28
240 | 2011-02-02 13:11 | Weather | Wind - wires slap/pole down | 0 | BVY | 1 | 0 | BVYSD | 29
240 | 2014-04-30 13:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVY | 1 | 0 | BVYSD | 27
240 | 2015-01-25 10:08 | Undetermined | Undetermined | 0 | BVY | 1 | 0 | BVYSD | 25
350 | 2008-11-06 10:46 | Undetermined | Undetermined | 0 | LLC | 1 | 0 | VLCC1 | 26
351 | 2007-01-05 17:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 1 | 0 | GOSC1 | 21
351 | 2007-10-22 03:46 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | TLK | 1 | 0 | VLCC1 | 52
354 | 2006-12-03 10:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LLC | 1 | 0 | GOSC1 | 37
355 | 2007-10-22 23:53 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0 | ANEC1 | 59
356 | 2006-02-08 12:31 | Undetermined | Undetermined | 0 | WAL | 1 | 0 | ANEC1 | 26
356 | 2007-10-22 16:00 | Weather | Wind - wires slap/pole down | 0 | WAL | 1 | 0 | ANEC1 | 59
357 | 2007-03-02 16:34 | Undetermined | Undetermined | 0 | PVD | 1 | 0 | ANEC1 | 38
357 | 2007-10-22 07:29 | Equipment | Connector/jumper/splice/elbow/rack | 0 | PVD | 1 | 0 | ANEC1 | 59
358 | 2007-10-21 21:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ANE | 1 | 0 | ANEC1 | 59
358 | 2007-10-22 06:41 | Weather | Wind - wires slap/pole down | 0 | ANE | 1 | 0 | ANEC1 | 59
358 | 2008-10-14 09:52 | Equipment | Crossarm failure | 0 | ANE | 1 | 0 | ANEC1 | 34
358 | 2009-01-11 23:13 | Undetermined | Undetermined | 0 | ANE | 1 | 0 | ANEC1 | 66
411 | 2007-10-23 09:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | cst | 1 | 0 | ANEC1 | 58
440 | 2006-01-05 20:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 1 | 0 | MLGC1 | 18
440 | 2014-05-01 09:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LAG | 1 | 0 | LAGSD | 56
441 | 2007-03-03 13:13 | Weather | Wind - wires slap/pole down | 0 | LPT | 1 | 0 | CMNC1 | 51
441 | 2007-10-22 02:39 | Weather | Wind - wires slap/pole down | 0 | LPT | 1 | 0 | CMNC1 | 58
441 | 2011-02-02 08:02 | Weather | Circuit Flashover/fog/foreign object | 0 | LPT | 1 | 0 | CMNC1 | 48
442 | 2007-10-22 00:11 | Weather | Wind - wires slap/pole down | 0 | SRH | 1 | 0 | CMNC1 | 58
442 | 2007-10-22 01:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 1 | 0 | CMNC1 | 58
442 | 2007-10-22 17:07 | Weather | Wind - wires slap/pole down | 0 | SRH | 1 | 0 | CMNC1 | 58
442 | 2009-01-10 21:02 | Weather | Wind - wires slap/pole down | 0 | SRH | 1 | 0 | CMNC1 | 50
442 | 2014-05-01 04:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 1 | 0 | SRHSD | 69
444 | 2007-03-02 19:57 | Undetermined | Undetermined | 0 | BVD | 1 | 0 | CMNC1 | 51
445 | 2006-01-23 09:23 | Equipment | Conductor failure/wire down | 0 | BVD | 1 | 0 | CMNC1 | 41
445 | 2007-10-21 20:16 | Weather | Wind - wires slap/pole down | 0 | BVD | 1 | 0 | CMNC1 | 58
445 | 2007-10-22 08:11 | Weather | Wind - wires slap/pole down | 0 | BVD | 1 | 0 | CMNC1 | 58
448 | 2007-10-22 09:57 | Weather | Wind - wires slap/pole down | 0 | WPT | 1 | 0 | POTC1 | 69
448 | 2007-10-23 12:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | WPT | 1 | 0 | POTC1 | 58
449 | 2008-10-14 04:52 | Undetermined | Undetermined | 0 | MOR | 1 | 0 | CMNC1 | 58
449 | 2014-04-30 10:06 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | MOR | 1 | 0 | MORSD | 53
470 | 2006-10-26 11:00 | Undetermined | Undetermined | 0 | HVW | 1 | 0 | KRNM | 35.04
470 | 2006-10-26 13:50 | Undetermined | Undetermined | 0 | HVW | 1 | 0 | KRNM | 35.04
470 | 2007-03-03 10:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVW | 1 | 0 | KRNM | 51.52
470 | 2007-03-03 16:34 | Weather | Wind - wires slap/pole down | 0 | HVW | 1 | 0 | KRNM | 51.52
470 | 2015-01-25 10:15 | Undetermined | Undetermined | 0 | HVW | 1 | 0 | HVWSD | 33
520 | 2007-01-05 11:42 | Undetermined | Undetermined | 0 | DLZ | 1 | 0 | SRUC1 | 48
520 | 2007-10-21 11:16 | Weather | Wind - wires slap/pole down | 0 | DLZ | 1 | 0 | SRUC1 | 36
524 | 2007-10-21 19:40 | Weather | Wind - wires slap/pole down | 0 | LSV | 1 | 0 | ANEC1 | 59
524 | 2007-10-22 06:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 1 | 0 | ANEC1 | 59
524 | 2007-10-22 12:43 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | LSV | 1 | 0 | ANEC1 | 59
73 | 2007-10-22 04:54 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 60
73 | 2014-04-30 06:18 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENSD | 53
75 | 2006-11-30 00:45 | Weather | Wind - wires slap/pole down | 0 | OTY | 1 | 0 | MIGC1 | 24
75 | 2007-03-03 10:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0 | MIGC1 | 35
75 | 2007-10-22 07:11 | Weather | Wind - wires slap/pole down | 0 | OTY | 1 | 0 | MIGC1 | 40
75 | 2008-12-09 12:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0 | MIGC1 | 26
75 | 2008-12-09 12:58 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0 | MIGC1 | 26
75 | 2008-12-09 14:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0 | MIGC1 | 26
75 | 2011-02-02 14:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0 | OTYSD | 29
75 | 2014-05-01 11:52 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 1 | 0 | OTYSD | 29
78 | 2006-11-30 07:26 | Equipment | Connector/jumper/splice/elbow/rack | 0 | VJS | 1 | 0 | ANEC1 | 33
78 | 2014-04-30 06:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VJS | 1 | 0 | VJSSD | 58
79 | 2005-03-31 10:55 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 48
79 | 2005-03-31 15:59 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 48
79 | 2007-10-21 22:30 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 60
79 | 2007-10-23 13:00 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 60
79 | 2007-10-23 19:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 50
79 | 2009-01-10 05:19 | Weather | Wind - wires slap/pole down | 0 | DEN | 1 | 0 | DENC1 | 52
79 | 2009-01-10 21:56 | Equipment | Insulator/pin failure/wire floating | 0 | DEN | 1 | 0 | DENC1 | 52
79 | 2009-01-11 00:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 50
79 | 2009-01-11 01:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENC1 | 50
79 | 2009-01-11 11:18 | Weather | Wind - wires slap/pole down | 0 | DEN | 1 | 0 | DENC1 | 50
79 | 2011-01-23 08:05 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENSD | 43
79 | 2011-02-03 13:31 | Undetermined | Undetermined | 0 | DEN | 1 | 0 | DENSD | 35
79 | 2014-04-30 06:21 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | DEN | 1 | 0 | DENSD | 53
79 | 2014-05-01 03:15 | Weather | Wind - wires slap/pole down | 0 | DEN | 1 | 0 | DENSD | 53
79 | 2015-01-24 07:44 | Equipment | Conductor contact/wire slap | 0 | DEN | 1 | 0 | DENSD | 44
908 | 2005-04-01 04:12 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 1 | 0 | VLCC1 | 41
908 | 2006-12-03 08:15 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 1 | 0 | GOSC1 | 37
908 | 2007-10-22 04:18 | Undetermined | Undetermined | 0 | HID | 1 | 0 | VLCC1 | 52
909 | 2007-03-03 13:34 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0 | GOSC1 | 37
909 | 2007-10-22 12:57 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0 | VLCC1 | 52
909 | 2007-10-23 14:29 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0 | VLCC1 | 50
909 | 2007-10-23 16:24 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | VLC | 1 | 0 | VLCC1 | 50
909 | 2008-01-01 08:46 | Weather | Wind - wires slap/pole down | 0 | VLC | 1 | 0 | VLCC1 | 45
909 | 2011-01-23 08:11 | Weather | Wind - wires slap/pole down | 0 | VLC | 1 | 0 | VLCSD | 26
909 | 2014-03-09 12:43 | Equipment | Insulator/pin failure/wire floating | 0 | VLC | 1 | 0 | VLCSD | 28
972 | 2006-01-23 08:21 | Equipment | Connector/jumper/splice/elbow/rack | 0 | HVY | 1 | 0 | KRNM | 35.04
972 | 2007-03-04 07:35 | Undetermined | Undetermined | 0 | HVY | 1 | 0 | KRNM | 51.52
972 | 2007-10-21 20:27 | Weather | Wind - wires slap/pole down | 0 | HVY | 1 | 0 | KRNM | 46.08
972 | 2007-10-22 06:31 | Weather | Wind - wires slap/pole down | 0 | HVY | 1 | 0 | KRNM | 57.12
972 | 2007-10-22 18:38 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HVY | 1 | 0 | KRNM | 42.4
972 | 2014-04-30 11:13 | Undetermined | Undetermined | 0 | HVY | 1 | 0 | HVYSD | 41
972 | 2015-01-24 12:00 | Undetermined | Undetermined | 0 | HVY | 1 | 0 | HVYSD | 40
972 | 2015-01-25 09:02 | Equipment | Conductor contact/wire slap | 0 | HVY | 1 | 0 | HVYSD | 40
974 | 2005-11-15 12:26 | Undetermined | Undetermined | 0 | BNA | 1 | 0 | GOSC1 | 26
974 | 2015-01-25 10:25 | Undetermined | Undetermined | 0 | BNA | 1 | 0 | BNASD | 34

## Vegetation
| Outages Occuring On Previously Identified Circuits (1981-2014) | [5 empty] | 2004-01-01
Circuit | Occurrence | Cause Category | Cause Description | Control Date | Station Code | FireWeather | 2005-01-01 | Bin | Frequency
1001 | 2009-12-07 16:28 | Weather | Tree fell on line due to storm/wind | 0 | RSF | 0 | 2006-01-01 | 2005-01-01 | 0
1001 | 2010-12-23 01:48 | Weather | Tree fell on line due to storm/wind | 0 | RSF | 0 | 2007-01-01 | 2006-01-01 | 18
1021 | 2012-12-13 03:48 | Foreign Object | Flashover/vegetation | 0 | HID | 0 | 2008-01-01 | 2007-01-01 | 18
1030 | 2009-12-07 05:25 | Weather | Palm frond contact due to storm/wind | 0 | HHC | 0 | 2009-01-01 | 2008-01-01 | 20
1030 | 2010-12-22 07:11 | Weather | Tree fell on line due to storm/wind | 0 | HHC | 0 | 2010-01-01 | 2009-01-01 | 22
1030 | 2010-12-29 14:37 | Weather | Tree fell on line due to storm/wind | 0 | HHC | 0 | 2011-01-01 | 2010-01-01 | 12
1094 | 2010-03-14 19:00 | Tree Contact | Tree fell on line | 0 | OLV | 0 | 2012-01-01 | 2011-01-01 | 25
1166 | 2012-02-15 17:57 | Foreign Object | Flashover/vegetation | 0 | LLD | 0 | 2013-01-01 | 2012-01-01 | 9
1458 | 2007-09-12 11:06 | Tree Contact | Palm tree contact | 0 | ANE | 0 | 2014-01-01 | 2013-01-01 | 12
157 | 2006-12-27 15:15 | Weather | Tree fell on line due to storm/wind | 0 | BAJC1 | 0 | 2015-01-01 | 2014-01-01 | 9
157 | 2010-08-02 12:18 | Tree Contact | Tree fell on line | 0 | BAJC1 | 0 | 2016-01-01 | 2015-01-01 | 17
157 | 2010-08-02 21:42 | Tree Contact | Tree fell on line | 0 | BAJC1 | 0 |  | 2016-01-01 | 3
157 | 2010-11-03 10:44 | Weather | Tree fell on line due to storm/wind | 0 | BAJC1 | 0 |  | More | 0
170 | 2008-02-03 13:41 | Weather | Tree fell on line due to storm/wind | 0 | BRG | 0 |  | Total | 165
170 | 2012-01-23 07:53 | Tree Contact | Tree fell on line | 0 | BRG | 0
172 | 2008-06-04 14:16 | Weather | Tree fell on line due to storm/wind | 0 | BRG | 0
175 | 2007-03-03 11:34 | Weather | Tree contact due to storm/high wind | 0 | ARH | 1
175 | 2010-03-02 13:16 | Tree Contact | Tree fell on line | 0 | ARH | 0
175 | 2014-12-30 17:34 | Tree Contact | Tree fell on line | 0 | ARH | 0
176 | 2007-08-13 15:53 | Tree Contact | Tree fell on line | 0 | ARH | 0
204 | 2005-12-03 06:37 | Tree Contact | Tree fell on line | 0 | CAP | 0
206 | 2005-01-07 12:01 | Weather | Tree fell on line due to storm/wind | 0 | CBD | 0
206 | 2005-01-11 03:43 | Weather | Tree fell on line due to storm/wind | 0 | CBD | 0
206 | 2006-01-02 12:40 | Weather | Palm frond contact due to storm/wind | 0 | CBD | 0
206 | 2008-02-14 18:02 | Tree Contact | Tree fell on line | 0 | CBD | 0
206 | 2010-01-20 17:57 | Tree Contact | Tree fell on line | 0 | CBD | 0
206 | 2010-01-22 19:42 | Weather | Tree fell on line due to storm/wind | 0 | CBD | 0
206 | 2010-12-20 18:28 | Weather | Tree fell on line due to storm/wind | 0 | CBD | 0
206 | 2010-12-30 02:41 | Weather | Tree fell on line due to storm/wind | 0 | CBD | 0
210 | 2006-07-22 21:21 | Weather | Tree contact due to storm/high wind | 0 | COY | 0
210 | 2011-07-30 15:28 | Weather | Tree fell on line due to storm/wind | 0 | COY | 0
211 | 2008-08-29 03:54 | Tree Contact | Tree fell on line | 0 | EWN | 0
211 | 2008-12-17 08:50 | Weather | Tree fell on line due to storm/wind | 0 | EWN | 0
211 | 2008-12-29 12:55 | Weather | Tree fell on line due to storm/wind | 0 | EWN | 0
214 | 2005-02-02 05:01 | Weather | Tree fell on line due to storm/wind | 0 | RIN | 0
214 | 2007-10-22 19:55 | Weather | Tree contact due to storm/high wind | 0 | RIN | 1
214 | 2008-12-18 02:04 | Weather | Tree fell on line due to storm/wind | 0 | RIN | 0
214 | 2009-01-09 23:06 | Weather | Tree fell on line due to storm/wind | 0 | RIN | 0
215 | 2009-12-07 14:25 | Weather | Tree fell on line due to storm/wind | 0 | RIN | 0
217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | PAU | 0
217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | RIN | 0
220 | 2006-03-28 23:24 | Weather | Tree fell on line due to storm/wind | 0 | YSA | 0
221 | 2007-10-26 08:39 | Tree Contact | Tree fell on line | 0 | YSA | 0
222 | 2005-09-21 07:20 | Tree Contact | Tree fell on line | 0 | YSA | 0
222 | 2007-09-02 14:26 | Tree Contact | Tree fell on line | 0 | YSA | 0
222 | 2008-01-07 03:40 | Weather | Tree fell on line due to storm/wind | 0 | YSA | 0
222 | 2008-10-23 15:46 | Weather | Tree fell on line due to storm/wind | 0 | YSA | 0
222 | 2008-12-17 09:21 | Weather | Tree fell on line due to storm/wind | 0 | YSA | 0
222 | 2009-03-22 15:51 | Weather | Tree fell on line due to storm/wind | 0 | YSA | 0
222 | 2011-02-27 08:27 | Weather | Tree fell on line due to storm/wind | 0 | YSA | 0
233 | 2006-07-28 04:19 | Tree Contact | Tree fell on line | 0 | FBK | 0
233 | 2007-04-18 09:31 | Tree Contact | Tree fell on line | 0 | FBK | 0
233 | 2007-10-21 14:03 | Weather | Tree contact due to storm/high wind | 0 | FBK | 1
233 | 2009-02-17 04:16 | Weather | Tree fell on line due to storm/wind | 0 | FBK | 0
233 | 2010-03-16 11:25 | Tree Contact | Tree fell on line | 0 | FBK | 0
233 | 2014-04-26 01:32 | Tree Contact | Tree fell on line | 0 | FBK | 0
236 | 2010-01-19 14:06 | Weather | Tree fell on line due to storm/wind | 0 | RAM | 0
236 | 2014-05-16 21:24 | Weather | Tree fell on line due to storm/wind | 0 | RAM | 0
237 | 2008-09-19 22:26 | Tree Contact | Tree fell on line | 0 | GOS | 0
237 | 2008-11-14 14:46 | Weather | Tree contact due to storm/high wind | 0 | GOS | 0
237 | 2014-11-02 17:19 | Tree Contact | Tree fell on line | 0 | GOS | 0
237 | 2015-02-12 20:06 | Tree Contact | Tree fell on line | 0 | GOS | 1
239 | 2007-08-05 11:38 | Tree Contact | Tree fell on line | 0 | FBK | 0
239 | 2007-10-13 05:35 | Weather | Tree fell on line due to storm/wind | 0 | FBK | 0
239 | 2009-01-12 22:49 | Weather | Tree fell on line due to storm/wind | 0 | FBK | 1
239 | 2010-12-22 15:07 | Weather | Tree fell on line due to storm/wind | 0 | FBK | 0
239 | 2011-05-19 16:55 | Tree Contact | Tree fell on line | 0 | FBK | 0
240 | 2009-10-08 11:05 | Tree Contact | Tree fell on line | 0 | BVY | 0
240 | 2012-02-12 10:50 | Tree Contact | Tree fell on line | 0 | BVY | 0
240 | 2013-02-08 06:51 | Foreign Object | Flashover/vegetation | 0 | BVY | 0
243 | 2008-01-23 19:14 | Weather | Tree fell on line due to storm/wind | 0 | BVY | 0
243 | 2010-01-21 12:17 | Weather | Tree fell on line due to storm/wind | 0 | BVY | 0
243 | 2011-02-02 13:38 | Weather | Tree fell on line due to storm/wind | 0 | BVY | 1
246 | 2010-12-26 03:15 | Weather | Tree fell on line due to storm/wind | 0 | BVY | 0
305 | 2006-06-10 21:25 | Tree Contact | Tree fell on line | 0 | RSF | 0
305 | 2006-11-29 22:51 | Weather | Tree fell on line due to storm/wind | 0 | RSF | 0
305 | 2009-02-09 16:47 | Weather | Tree fell on line due to storm/wind | 0 | RSF | 0
307 | 2005-02-19 16:49 | Weather | Tree fell on line due to storm/wind | 0 | RSF | 0
307 | 2008-02-22 11:53 | Tree Contact | Tree fell on line | 0 | RSF | 0
307 | 2012-03-18 05:06 | Weather | Tree fell on line due to storm/wind | 0 | RSF | 0
311 | 2006-02-07 21:34 | Weather | Tree fell on line due to storm/wind | 0 | CAP | 1
323 | 2014-04-29 16:48 | Weather | Tree fell on line due to storm/wind | 0 | MIG | 0
350 | 2005-05-02 16:13 | Weather | Palm frond contact due to storm/wind | 0 | LLC | 0
350 | 2006-01-02 12:55 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
350 | 2006-12-12 12:57 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
350 | 2008-12-15 12:57 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
350 | 2008-12-17 12:55 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
350 | 2010-01-18 13:31 | Weather | Tree contact due to storm/high wind | 0 | LLC | 0
350 | 2010-01-19 14:00 | Weather | Tree contact due to storm/high wind | 0 | LLC | 0
350 | 2011-05-30 17:26 | Tree Contact | Tree contact | 0 | LLC | 0
350 | 2012-02-14 06:04 | Foreign Object | Flashover/vegetation | 0 | LLC | 0
351 | 2005-04-06 18:30 | Tree Contact | Tree fell on line | 0 | TLK | 0
351 | 2006-11-29 20:54 | Weather | Tree fell on line due to storm/wind | 0 | TLK | 0
351 | 2007-02-17 12:45 | Tree Contact | Tree fell on line | 0 | TLK | 0
351 | 2007-03-04 09:24 | Weather | Tree fell on line due to storm/wind | 0 | TLK | 1
351 | 2012-12-29 22:05 | Weather | Tree fell on line due to storm/wind | 0 | TLK | 0
351 | 2015-03-10 18:23 | Tree Contact | Tree fell on line | 0 | TLK | 0
352 | 2005-06-21 07:50 | Tree Contact | Tree fell on line | 0 | LLC | 0
352 | 2010-05-19 10:15 | Tree Contact | Tree fell on line | 0 | LLC | 0
353 | 2006-04-05 05:53 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
353 | 2006-05-28 06:19 | Tree Contact | Tree fell on line | 0 | LLC | 0
353 | 2014-02-28 10:34 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
353 | 2014-11-01 03:59 | Weather | Tree fell on line due to storm/wind | 0 | LLC | 0
356 | 2005-03-20 07:45 | Tree Contact | Tree contact | 0 | WAL | 0
356 | 2009-09-23 10:04 | Tree Contact | Tree fell on line | 0 | WAL | 0
356 | 2012-03-17 14:17 | Weather | Tree fell on line due to storm/wind | 0 | WAL | 0
356 | 2012-03-18 15:49 | Weather | Tree fell on line due to storm/wind | 0 | WAL | 0
357 | 2008-01-27 09:21 | Weather | Tree fell on line due to storm/wind | 0 | PVD | 0
357 | 2009-08-25 14:11 | Tree Contact | Tree fell on line | 0 | PVD | 0
357 | 2009-12-07 15:26 | Weather | Tree fell on line due to storm/wind | 0 | PVD | 0
357 | 2010-02-21 12:17 | Foreign Object | Flashover/vegetation | 0 | PVD | 0
357 | 2014-04-30 06:17 | Weather | Tree fell on line due to storm/wind | 0 | PVD | 1
411 | 2010-02-10 11:11 | Tree Contact | Palm frond contact | 0 | cst | 0
411 | 2010-02-28 10:56 | Tree Contact | Tree fell on line | 0 | cst | 0
411 | 2013-01-25 06:08 | Foreign Object | Flashover/vegetation | 0 | cst | 0
440 | 2011-02-20 07:57 | Weather | Tree fell on line due to storm/wind | 0 | LAG | 0
441 | 2010-04-07 06:35 | Tree Contact | Tree fell on line | 0 | LPT | 0
442 | 2013-09-05 14:00 | Weather | Tree fell on line due to storm/wind | 0 | SRH | 0
442 | 2014-04-30 06:11 | Weather | Tree fell on line due to storm/wind | 0 | SRH | 1
444 | 2013-03-28 14:02 | Foreign Object | Flashover/vegetation | 0 | BVD | 0
445 | 2013-07-30 12:45 | Tree Contact | Tree fell on line | 0 | BVD | 0
448 | 2014-04-29 08:44 | Weather | Tree fell on line due to storm/wind | 0 | WPT | 0
450 | 2005-02-22 11:23 | Weather | Tree contact due to storm/high wind | 0 | ESC | 0
450 | 2005-11-25 15:53 | Tree Contact | Tree fell on line | 0 | ESC | 0
450 | 2006-01-02 20:33 | Weather | Tree fell on line due to storm/wind | 0 | ESC | 0
450 | 2007-06-13 15:30 | Tree Contact | Tree fell on line | 0 | ESC | 0
450 | 2012-01-16 06:40 | Weather | Tree fell on line due to storm/wind | 0 | ESC | 0
450 | 2013-11-02 01:58 | Tree Contact | Tree fell on line | 0 | ESC | 0
456 | 2006-11-29 18:29 | Weather | Palm frond contact due to storm/wind | 0 | ESC | 0
470 | 2005-04-29 05:18 | Weather | Tree fell on line due to storm/wind | 0 | HVW | 0
470 | 2007-04-23 02:55 | Weather | Tree fell on line due to storm/wind | 0 | HVW | 0
470 | 2014-04-30 13:07 | Weather | Tree fell on line due to storm/wind | 0 | HVW | 1
520 | 2006-01-15 14:18 | Weather | Tree fell on line due to storm/wind | 0 | DLZ | 0
520 | 2008-10-14 08:58 | Weather | Tree fell on line due to storm/wind | 0 | DLZ | 1
520 | 2012-03-19 05:54 | Weather | Tree fell on line due to storm/wind | 0 | DLZ | 0
520 | 2014-02-13 18:22 | Tree Contact | Tree fell on line | 0 | DLZ | 0
520 | 2014-03-31 15:38 | Tree Contact | Tree fell on line | 0 | DLZ | 0
520 | 2015-01-05 15:25 | Tree Contact | Tree fell on line | 0 | DLZ | 0
521 | 2005-02-03 10:13 | Weather | Tree fell on line due to storm/wind | 0 | RBV | 0
521 | 2008-11-27 04:44 | Tree Contact | Tree fell on line | 0 | RBV | 0
521 | 2012-05-28 06:29 | Tree Contact | Tree fell on line | 0 | RBV | 0
701 | 2007-12-07 05:51 | Weather | Palm frond contact due to storm/wind | 0 | MVN | 0
73 | 2005-06-21 19:52 | Tree Contact | Tree fell on line | 0 | DEN | 0
75 | 2007-03-03 07:53 | Weather | Tree fell on line due to storm/wind | 0 | OTY | 1
79 | 2007-04-10 07:12 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 0
79 | 2008-10-13 23:55 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 1
79 | 2008-12-18 03:41 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 0
79 | 2011-02-27 02:35 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 0
79 | 2014-03-09 11:30 | Tree Contact | Tree fell on line | 0 | DEN | 1
79 | 2014-03-09 18:34 | Tree Contact | Tree fell on line | 0 | DEN | 1
79 | 2014-04-30 01:17 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 1
907 | 2014-06-24 12:47 | Tree Contact | Tree fell on line | 0 | VLC | 0
908 | 2005-04-01 06:08 | Weather | Tree contact due to storm/high wind | 0 | HID | 1
908 | 2005-07-03 15:05 | Tree Contact | Tree fell on line | 1 | HID | 0
908 | 2007-03-04 09:49 | Weather | Palm tree contact due to storm/wind | 0 | HID | 1
908 | 2007-06-12 00:50 | Tree Contact | Tree contact | 0 | HID | 0
908 | 2011-11-02 08:09 | Weather | Tree fell on line due to storm/wind | 0 | HID | 0
920 | 2005-03-31 09:18 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 1
920 | 2006-12-02 18:39 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 1
920 | 2007-01-06 09:38 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 1
920 | 2008-12-16 16:08 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 0
920 | 2013-09-16 07:19 | Tree Contact | Tree fell on line | 0 | SYC | 0
971 | 2006-06-29 16:49 | Tree Contact | Tree fell on line | 0 | MGR | 0
972 | 2010-01-19 14:26 | Weather | Tree fell on line due to storm/wind | 0 | HVY | 0
CTL1 | 2011-02-27 12:02 | Weather | Tree fell on line due to storm/wind | 0 | PAM | 0

## VegFWO
Circuit | Occurrence | Cause Category | Cause Description | Control Date | Station Code | FireWeather | Actv Station | 2004-01-01 | Bin | Frequency | Total | Bkgds | Bkgds/yr
175 | 2007-03-03 11:34 | Weather | Tree contact due to storm/high wind | 0 | ARH | 1 | KRNM | 2005-01-01 | 2005-01-01 | 0 | 21 | 4.1457 | 0.40446
214 | 2007-10-22 19:55 | Weather | Tree contact due to storm/high wind | 0 | RIN | 1 | VLCC1 | 2006-01-01 | 2006-01-01 | 2
233 | 2007-10-21 14:03 | Weather | Tree contact due to storm/high wind | 0 | FBK | 1 | SRUC1 | 2007-01-01 | 2007-01-01 | 2
237 | 2015-02-12 20:06 | Tree Contact | Tree fell on line | 0 | GOS | 1 | GOSSD | 2008-01-01 | 2008-01-01 | 6
239 | 2009-01-12 22:49 | Weather | Tree fell on line due to storm/wind | 0 | FBK | 1 | SRUC1 | 2009-01-01 | 2009-01-01 | 2
243 | 2011-02-02 13:38 | Weather | Tree fell on line due to storm/wind | 0 | BVY | 1 | BVYSD | 2010-01-01 | 2010-01-01 | 1
311 | 2006-02-07 21:34 | Weather | Tree fell on line due to storm/wind | 0 | CAP | 1 | CAPC1 | 2011-01-01 | 2011-01-01 | 0
351 | 2007-03-04 09:24 | Weather | Tree fell on line due to storm/wind | 0 | TLK | 1 | VLCC1 | 2012-01-01 | 2012-01-01 | 1
357 | 2014-04-30 06:17 | Weather | Tree fell on line due to storm/wind | 0 | PVD | 1 | PVDSD | 2013-01-01 | 2013-01-01 | 0
442 | 2014-04-30 06:11 | Weather | Tree fell on line due to storm/wind | 0 | SRH | 1 | SRHSD | 2014-01-01 | 2014-01-01 | 0
470 | 2014-04-30 13:07 | Weather | Tree fell on line due to storm/wind | 0 | HVW | 1 | HVWSD | 2015-01-01 | 2015-01-01 | 6
520 | 2008-10-14 08:58 | Weather | Tree fell on line due to storm/wind | 0 | DLZ | 1 | SRUC1 | 2016-01-01 | 2016-01-01 | 1
75 | 2007-03-03 07:53 | Weather | Tree fell on line due to storm/wind | 0 | OTY | 1 | MIGC1 |  | More | 0
79 | 2008-10-13 23:55 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 1 | DENC1
79 | 2014-03-09 11:30 | Tree Contact | Tree fell on line | 0 | DEN | 1 | DENSD
79 | 2014-03-09 18:34 | Tree Contact | Tree fell on line | 0 | DEN | 1 | DENSD
79 | 2014-04-30 01:17 | Weather | Tree fell on line due to storm/wind | 0 | DEN | 1 | DENSD
908 | 2005-04-01 06:08 | Weather | Tree contact due to storm/high wind | 0 | HID | 1 | VLCC1
908 | 2007-03-04 09:49 | Weather | Palm tree contact due to storm/wind | 0 | HID | 1 | VLCC1
920 | 2005-03-31 09:18 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 1 | MPEC1
920 | 2006-12-02 18:39 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 1 | MPEC1
920 | 2007-01-06 09:38 | Weather | Tree fell on line due to storm/wind | 0 | SYC | 1 | MPEC1

## Reclosers
Circuit | Occurrence | Cause Category | Cause Description | Control Date | Station Code | FireWeather | Reclose
217 | 2006-01-23 19:44 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 1 | 1
1250 | 2005-01-20 11:12 | Equipment | Conductor failure/wire down | 0 | RSF | 0 | 1
172 | 2012-01-21 14:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 1 | 2005-01-01 | 38353 | Frequency | Rate
172 | 2012-01-21 14:20 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BRG | 0 | 1 | 2006-01-01 | 2006-01-01 | 218 | 210.439
172 | 2012-01-21 14:21 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 1 | 2007-01-01 | 2007-01-01 | 222
172 | 2013-04-08 09:05 | Weather | Wind - wires slap/pole down | 0 | BRG | 0 | 1 | 2008-01-01 | 2008-01-01 | 244
175 | 2008-12-17 11:15 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1 | 2009-01-01 | 2009-01-01 | 216
175 | 2008-12-17 11:20 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1 | 2010-01-01 | 2010-01-01 | 201
175 | 2008-12-17 11:25 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1 | 2011-01-01 | 2011-01-01 | 270
175 | 2008-12-17 11:30 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1 | 2012-01-01 | 2012-01-01 | 198
175 | 2008-12-17 11:37 | Weather | Wind - wires slap/pole down | 0 | ARH | 0 | 1 | 2013-01-01 | 2013-01-01 | 231
176 | 2010-09-30 13:26 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 1 | 2014-01-01 | 2014-01-01 | 180
176 | 2010-09-30 13:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | ARH | 0 | 1 | 2015-01-01 | 2015-01-01 | 218
211 | 2012-04-14 06:53 | Undetermined | Undetermined | 0 | EWN | 0 | 1 | 2016-01-01 | 2016-01-01 | 39
211 | 2012-04-14 07:03 | Undetermined | Undetermined | 0 | EWN | 0 | 1 |  | More | 0
211 | 2012-04-14 07:10 | Undetermined | Undetermined | 0 | EWN | 0 | 1 | 2015-03-15 | Total | 2237
217 | 2005-05-03 20:04 | Undetermined | Undetermined | 0 | RIN | 0 | 1 |  | No Recl. | 2157
1030 | 2007-10-22 00:45 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HHC | 1 | 1
217 | 2006-01-24 12:32 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2006-05-05 17:55 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-06-04 04:14 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-09-22 13:45 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-11-26 16:34 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2006-12-09 21:48 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2007-07-05 01:46 | Equipment | Connector/jumper/splice/elbow/rack | 1 | RIN | 0 | 1
217 | 2007-09-11 10:21 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2007-09-21 03:23 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2007-09-29 18:34 | Equipment | Conductor contact/wire slap | 0 | RIN | 0 | 1
217 | 2008-11-18 19:28 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2008-12-25 11:12 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2009-02-04 14:07 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2009-06-03 11:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 16:10 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 16:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | PAU | 0 | 1
217 | 2009-06-03 16:11 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 16:35 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2009-06-03 19:36 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2010-09-04 14:07 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2010-10-19 09:50 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2010-11-12 18:49 | Equipment | Cutout failure | 0 | RIN | 0 | 1
236 | 2008-01-01 08:17 | Weather | Wind - wires slap/pole down | 0 | RAM | 1 | 1
217 | 2011-01-26 19:31 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-03-02 10:50 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-05-29 05:06 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-06-11 10:30 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2011-07-03 03:25 | Undetermined | Undetermined | 1 | RIN | 0 | 1
217 | 2012-03-20 03:37 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 1
217 | 2012-04-19 07:26 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2013-01-08 12:01 | Equipment | Cutout failure | 0 | RIN | 0 | 1
217 | 2013-01-13 07:50 | Equipment | Conductor failure/wire down | 0 | RIN | 0 | 1
217 | 2013-02-24 11:56 | Foreign Object | Flashover/vegetation | 0 | RIN | 0 | 1
217 | 2013-12-27 14:35 | Equipment | Pole broke/rotted/on fire | 0 | RIN | 0 | 1
217 | 2014-02-28 18:31 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2014-04-29 16:34 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 1
217 | 2011-01-23 06:44 | Equipment | Conductor failure/wire down | 0 | RIN | 1 | 1
217 | 2014-04-30 08:11 | Undetermined | Undetermined | 0 | RIN | 1 | 1
217 | 2014-05-14 12:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RIN | 0 | 1
217 | 2014-07-21 15:54 | Undetermined | Undetermined | 0 | RIN | 0 | 1
217 | 2014-12-20 12:41 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 0 | 1
217 | 2014-04-30 11:21 | Equipment | Conductor failure/wire down | 0 | RIN | 1 | 1
217 | 2015-01-24 04:28 | Equipment | Connector/jumper/splice/elbow/rack | 0 | RIN | 1 | 1
217 | 2015-01-24 07:04 | Equipment | Conductor contact/wire slap | 0 | RIN | 1 | 1
217 | 2015-01-24 09:26 | Undetermined | Undetermined | 0 | RIN | 1 | 1
217 | 2015-01-24 14:23 | Equipment | Conductor contact/wire slap | 0 | RIN | 1 | 1
353 | 2012-12-13 12:48 | Equipment | Crossarm failure | 0 | LLC | 0 | 1
442 | 2012-02-28 02:47 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | SRH | 0 | 1
445 | 2011-07-05 17:27 | Undetermined | Undetermined | 1 | BVD | 0 | 1
445 | 2012-02-27 21:08 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 1
445 | 2012-02-27 21:14 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | BVD | 0 | 1
445 | 2012-02-27 21:34 | Weather | Wind - wires slap/pole down | 0 | BVD | 0 | 1
75 | 2008-01-07 00:42 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | OTY | 0 | 1
908 | 2010-10-19 02:09 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | HID | 0 | 1
974 | 2015-01-25 10:32 | Undetermined | Undetermined | 0 | BNA | 1 | 1
974 | 2015-01-25 10:51 | Undetermined | Undetermined | 0 | BNA | 1 | 1
RB1 | 2007-07-02 14:30 | Undetermined | Undetermined | 1 | RNB | 0 | 1
RB1 | 2009-12-02 06:29 | Equipment | Conductor failure/wire down | 0 | RNB | 0 | 1
RB1 | 2011-07-05 02:29 | Undetermined | Undetermined | 1 | RNB | 0 | 1
RB1 | 2011-09-08 13:10 | Undetermined | Undetermined | 0 | RNB | 0 | 1
RB1 | 2013-02-01 05:39 | Equipment | Conductor contact/wire slap | 0 | RNB | 0 | 1
RB1 | 2013-02-01 07:13 | Equipment | Conductor contact/wire slap | 0 | RNB | 0 | 1
RB1 | 2013-06-28 12:33 | Weather | Circ. Flashover/storm/high winds/undet. | 0 | RNB | 0 | 1

## Circuits
Circuit | ExtCauseExcl | FireWeather | Vegetation | VegFWO | HazSgmt | HazLgth | Out/L-Y | FWO/L-Y | Veg/L-Y | VFWO/L-Y | Med Risk
1001 | 12 | 0 | 2 | 0 | 2 | 6.8941 | 16.9816 | 0 | 2.8303 | 0 | 1.5624 | 1
1021 | 8 | 1 | 1 | 0 | 2 | 29.189 | 2.6739 | 13.3029 | 0.33424 | 0 | 1.9309 | 1.1
1030 | 29 | 4 | 3 | 0 | 3 | 77.4739 | 3.6519 | 20.0479 | 0.37778 | 0 | 2.2732 | 1.2
1094 | 3 | 0 | 1 | 0 | 0 | 0 |  |  |  |  | FALSE | 1.3
1100 | 5 | 0 | 0 | 0 | 2 | 3.6587 | 13.3327 | 0 | 0 | 0 | 1.17 | 1.4
1101 | 2 | 2 | 0 | 0 | 1 | 3.0506 | 6.3962 | 254.5741 | 0 | 0 | 1.28 | 1.5
1166 | 15 | 0 | 1 | 0 | 3 | 23.4049 | 6.2526 | 0 | 0.41684 | 0 | 2.0186 | 1.6
1215 | 32 | 4 | 0 | 0 | 1 | 21.9858 | 14.1999 | 70.6452 | 0 | 0 | 2.1198 | 1.7
1233 | 8 | 0 | 0 | 0 | 2 | 27.7496 | 2.8126 | 0 | 0 | 0 | 2.2408 | 1.8
1234 | 5 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE | 1.9
1250 | 13 | 0 | 0 | 0 | 1 | 15.9405 | 7.9564 | 0 | 0 | 0 | 2.1098 | 2
1458 | 12 | 3 | 1 | 0 | 2 | 17.8972 | 6.5414 | 65.0882 | 0.54512 | 0 | 1.9742 | 2.1
157 | 42 | 5 | 4 | 0 | 4 | 111.1663 | 3.686 | 17.4647 | 0.35105 | 0 | 2.0963 | 2.2
170 | 33 | 1 | 2 | 0 | 0 | 0 |  |  |  |  | FALSE | 2.3
172 | 38 | 1 | 1 | 0 | 0 | 0 |  |  |  |  | FALSE | 2.4
175 | 41 | 1 | 3 | 1 | 2 | 35.0165 | 11.4232 | 11.089 | 0.83584 | 11.089 | 2.0187 | 2.5
176 | 34 | 0 | 1 | 0 | 3 | 59.0536 | 5.6171 | 0 | 0.16521 | 0 | 1.9656
181 | 3 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
204 | 17 | 1 | 1 | 0 | 4 | 33.1123 | 5.0088 | 11.7267 | 0.29464 | 0 | 1.4743
206 | 22 | 2 | 8 | 0 | 1 | 4.8136 | 44.5888 | 161.3324 | 16.2141 | 0 | 1.12
210 | 23 | 1 | 2 | 0 | 3 | 20.5477 | 10.9204 | 18.8974 | 0.9496 | 0 | 1.8888
211 | 39 | 1 | 3 | 0 | 3 | 45.7633 | 8.3143 | 8.4849 | 0.63956 | 0 | 1.9535
212 | 74 | 0 | 0 | 0 | 6 | 112.4735 | 6.4189 | 0 | 0 | 0 | 1.9687
214 | 32 | 2 | 4 | 1 | 5 | 61.0455 | 5.1141 | 12.7216 | 0.63927 | 6.3608 | 2.0445
215 | 16 | 0 | 1 | 0 | 2 | 23.9036 | 6.5303 | 0 | 0.40814 | 0 | 1.8967
216 | 10 | 4 | 0 | 0 | 1 | 6.6792 | 14.6068 | 232.5427 | 0 | 0 | 1.8099
217 | 92 | 8 | 2 | 0 | 2 | 71.8917 | 12.4849 | 43.2092 | 0.27141 | 0 | 2.1
220 | 37 | 4 | 1 | 0 | 3 | 52.2633 | 6.9069 | 29.7186 | 0.18667 | 0 | 2.1594
221 | 85 | 3 | 1 | 0 | 5 | 87.1208 | 9.5186 | 13.371 | 0.11198 | 0 | 2.0039
222 | 114 | 10 | 7 | 0 | 3 | 103.9066 | 10.7038 | 37.3699 | 0.65725 | 0 | 2.2417
233 | 35 | 1 | 6 | 1 | 3 | 63.4199 | 5.3842 | 6.1227 | 0.923 | 6.1227 | 1.7593
235 | 11 | 1 | 0 | 0 | 1 | 14.8273 | 7.2378 | 26.1881 | 0 | 0 | 1.5499
236 | 42 | 6 | 2 | 0 | 1 | 45.9146 | 8.9243 | 50.7418 | 0.42497 | 0 | 2.2695
237 | 33 | 2 | 4 | 1 | 3 | 75.8794 | 4.2429 | 10.2346 | 0.5143 | 5.1173 | 2.1765
239 | 38 | 4 | 5 | 1 | 3 | 52.9468 | 7.002 | 29.335 | 0.92131 | 7.3337 | 1.9836
240 | 35 | 4 | 3 | 0 | 3 | 36.3239 | 9.4005 | 42.7595 | 0.80576 | 0 | 2.0044
243 | 6 | 0 | 3 | 1 | 0 | 0 |  |  |  |  | FALSE
246 | 16 | 0 | 1 | 0 | 2 | 20.7165 | 7.5349 | 0 | 0.47093 | 0 | 1.4937
283 | 16 | 0 | 0 | 0 | 3 | 18.6943 | 8.35 | 0 | 0 | 0 | 1.5665
305 | 8 | 0 | 3 | 0 | 0 | 0 |  |  |  |  | FALSE
307 | 1 | 0 | 3 | 0 | 3 | 10.165 | 0.95978 | 0 | 2.8793 | 0 | 1.4196
311 | 6 | 0 | 1 | 1 | 0 | 0 |  |  |  |  | FALSE
320 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
321 | 5 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
322 | 9 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
323 | 4 | 0 | 1 | 0 | 0 | 0 |  |  |  |  | FALSE
324 | 3 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
339 | 3 | 0 | 0 | 0 | 1 | 9.4475 | 3.098 | 0 | 0 | 0 | 1.3899
350 | 65 | 1 | 9 | 0 | 5 | 112.2981 | 5.647 | 3.4577 | 0.78189 | 0 | 1.8938
351 | 14 | 2 | 6 | 1 | 2 | 21.2756 | 6.4198 | 36.5018 | 2.7514 | 18.2509 | 2.0402
352 | 15 | 0 | 2 | 0 | 1 | 11.4432 | 12.7885 | 0 | 1.7051 | 0 | 1.9999
353 | 14 | 0 | 4 | 0 | 2 | 18.8172 | 7.2585 | 0 | 2.0739 | 0 | 1.9561
354 | 22 | 1 | 0 | 0 | 3 | 58.1455 | 3.6913 | 6.678 | 0 | 0 | 1.9718
355 | 6 | 1 | 0 | 0 | 1 | 13.5146 | 4.3314 | 28.7318 | 0 | 0 | 2.0899
356 | 24 | 2 | 4 | 0 | 2 | 27.1218 | 8.6331 | 28.6337 | 1.4389 | 0 | 2.0027
357 | 22 | 2 | 5 | 1 | 3 | 28.7508 | 7.4653 | 27.0113 | 1.6967 | 13.5057 | 2.2206
358 | 14 | 4 | 0 | 0 | 2 | 29.1985 | 4.6778 | 53.1942 | 0 | 0 | 2.209
374 | 7 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
378 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FALSE
411 | 16 | 1 | 3 | 0 | 3 | 26.7277 | 5.8403 | 14.5279 | 1.0951 | 0 | 1.9332
440 | 27 | 2 | 1 | 0 | 2 | 20.3271 | 12.9588 | 38.205 | 0.47996 | 0 | 2.2384
441 | 15 | 3 | 1 | 0 | 3 | 23.7017 | 6.1743 | 49.1481 | 0.41162 | 0 | 1.8985
442 | 28 | 5 | 2 | 1 | 3 | 28.5284 | 9.5754 | 68.0546 | 0.68396 | 13.6109 | 2.314
444 | 41 | 1 | 1 | 0 | 3 | 38.0195 | 10.5209 | 10.2131 | 0.25661 | 0 | 1.8457
445 | 68 | 3 | 1 | 0 | 6 | 94.9172 | 6.9894 | 12.2727 | 0.10279 | 0 | 1.8908
448 | 36 | 2 | 1 | 0 | 5 | 80.1966 | 4.3795 | 9.6837 | 0.12165 | 0 | 2.1815
449 | 21 | 2 | 0 | 0 | 3 | 31.0822 | 6.5915 | 24.9852 | 0 | 0 | 2.0532
450 | 12 | 0 | 6 | 0 | 1 | 8.5977 | 13.6168 | 0 | 6.8084 | 0 | 1.5599
470 | 24 | 5 | 3 | 1 | 2 | 28.7392 | 8.1473 | 67.5554 | 1.0184 | 13.5111 | 1.8909
48 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
500 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
520 | 50 | 2 | 6 | 1 | 8 | 114.1138 | 4.2747 | 6.8054 | 0.51297 | 3.4027 | 2.0561
521 | 36 | 0 | 3 | 0 | 6 | 76.8608 | 4.5696 | 0 | 0.3808 | 0 | 1.7203
524 | 44 | 3 | 0 | 0 | 3 | 72.0638 | 5.9568 | 16.1647 | 0 | 0 | 2.155
67 | 20 | 0 | 0 | 0 | 2 | 47.9754 | 4.0671 | 0 | 0 | 0 | 1.7867
701 | 4 | 0 | 1 | 0 | 0 | 0 |  |  |  |  | 0
728 | 3 | 0 | 0 | 0 | 1 | 2.086 | 14.0309 | 0 | 0 | 0 | 1.36
73 | 20 | 2 | 1 | 0 | 3 | 53.9665 | 3.6156 | 14.3903 | 0.18078 | 0 | 2.1749
75 | 57 | 8 | 1 | 1 | 4 | 57.3667 | 9.6937 | 54.1496 | 0.17007 | 6.7687 | 1.6426
78 | 6 | 2 | 0 | 0 | 1 | 12.1587 | 4.8144 | 63.8715 | 0 | 0 | 1.9099
79 | 98 | 15 | 7 | 4 | 7 | 64.5828 | 14.8042 | 90.1861 | 1.0574 | 24.0496 | 1.8212
907 | 13 | 0 | 1 | 0 | 2 | 18.2822 | 6.9373 | 0 | 0.53364 | 0 | 2.0862
908 | 43 | 3 | 5 | 2 | 2 | 71.4172 | 5.8741 | 16.3111 | 0.68304 | 10.8741 | 1.9903
909 | 23 | 7 | 0 | 0 | 2 | 28.5648 | 7.8555 | 95.1551 | 0 | 0 | 1.6333
92 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
920 | 9 | 0 | 5 | 3 | 2 | 6.9131 | 12.7013 | 0 | 7.0563 | 168.506 | 1.6198
970 | 3 | 0 | 0 | 0 | 1 | 2.2697 | 12.8952 | 0 | 0 | 0 | 1.09
971 | 21 | 0 | 1 | 0 | 4 | 108.4911 | 1.8884 | 0 | 0.089925 | 0 | 2.2296
972 | 45 | 8 | 1 | 0 | 4 | 53.2699 | 8.2415 | 58.3141 | 0.18314 | 0 | 1.9776
973 | 23 | 0 | 0 | 0 | 2 | 23.2523 | 9.6502 | 0 | 0 | 0 | 1.7862
974 | 15 | 2 | 0 | 0 | 2 | 21.5267 | 6.7981 | 36.0759 | 0 | 0 | 2
984 | 14 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
CTL1 | 1 | 0 | 1 | 0 | 1 | 4.1521 | 2.3497 | 0 | 2.3497 | 0 | 2
RB1 | 14 | 0 | 0 | 0 | 2 | 15.3248 | 8.9127 | 0 | 0 | 0 | 1.7491
TM1 | 12 | 0 | 0 | 0 | 1 | 2.9864 | 39.2026 | 0 | 0 | 0 | 1.94

## WeatherStations
Station Code | Station ID | Station Name | State | Reported in 24 hours? | First Data Date | Last Data Date | MesoWest Status | Latitude | Longitude | Elevation | Nearest RAWS | RAWS Elev | Dist/Dir
ANE | ANESD | Alpine | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.827 | -116.7733 | 1823 | ANEC1 | 2810 | 6 mi E
ARH | ARHSD | Archie Moore | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.0398 | -116.958 | 1479 | KRNM | 1391 | 2 mi E
BAJC1 | BAJC1 | Barrett |  |  | 2009-10-07 |  |  | 32.6675 | -116.6994 | 2395 | POTC1 | 2345 | 7 mi SE
BNA | BNASD | Barona | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.935 | -116.8759 | 1320 | GOSC1 | 1835 | 10 mi N
BRG | BRGSD | Borrego | CA | YES | 2011-09-28 | 2015-04-04 | ACTIVE | 33.262 | -116.3481 | 720 | FHCC1 | 781 | 25 mi SE
BVD | BVDSD | Boulevard West | CA | YES | 2010-08-30 | 2015-04-04 | ACTIVE | 32.6621 | -116.2889 | 3404 | CMNC1 | 3268 | 11 mi WNW
BVY | BVYSD | Blossom Valley | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8683 | -116.8425 | 1192 | ANEC1 | 2810 | 10 mi ESE
CAP | CAPSD | Bell Canyon | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.5576 | -117.5465 | 505 | CAPC1 | 793 | 2 mi WSW
CBD | CBDSD | Carlsbad | CA | YES | 2012-01-01 | 2015-04-04 | ACTIVE | 33.1374 | -117.3272 | 72 | KCRQ | 328 | 3 mi E
COY | COYSD | Los Coyotes | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.2584 | -116.5852 | 3815 | RCHC1 | 4415 | 6 mi SE
cst | cstSD | Crest | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8115 | -116.8532 | 1486 | ANEC1 | 2810 | 11 mi E
CWD | CWDSD | Crestwood | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.7008 | -116.3683 | 4088 | CMNC1 | 3268 | 6 mi WNW
DEN | DENSD | Descanso | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8588 | -116.6118 | 3393 | DENC1 | 3567 | 1 mi W
DHV | DHVSD | Deerhorn Valley | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.687 | -116.7622 | 2385 | OTYC1 | 3283 | 8 mi SWE
DLZ | DLZSD | Deluz | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.4584 | -117.2973 | 606 | SRUC1 | 1987 | 6 mi NE
DMH | DMHSD | Del Mar Heights | CA | YES | 2011-09-30 | 2015-04-04 | ACTIVE | 32.964 | -117.223 | 295 | LJPC1 | 0 | 7 mi SSW
ESC | ESCSD | Escondido | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.1592 | -117.0313 | 723 | VLCC1 | 1483 | 6 mi NNE
EWN | EWNSD | East Warners | CA | YES | 2011-08-02 | 2015-04-04 | ACTIVE | 33.2265 | -116.612 | 3242 | RCHC1 | 4415 | 7 mi E
FBK | FBKSD | Fallbrook | CA | YES | 2010-01-26 | 2015-04-04 | ACTIVE | 33.3547 | -117.1672 | 953 | SRUC1 | 1987 | 12 mi NNW
GOS | GOSSD | Goose Valley | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.0728 | -116.8449 | 1536 | GOSC1 | 1835 | 2 mi WNW
HHC | HHCSD | Hellhole Canyon | CA | YES | 2012-01-01 | 2015-04-04 | ACTIVE | 33.2244 | -116.9235 | 2001 | VLCC1 | 1483 | 5 mi W
HID | HIDSD | Hideaway Lake | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 33.24 | -117.0452 | 1422 | VLCC1 | 1483 | 2 mi E
HVW | HVWSD | Highland Valley West | CA | YES | 2012-01-01 | 2015-04-04 | ACTIVE | 33.0671 | -116.9901 | 1139 | KRNM | 1391 | 5 mi ESE
HVY | HVYSD | Highland Valley | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 33.0293 | -116.9352 | 1358 | KRNM | 1391 | 1 mi ENE
KSAN | KSAN | San Diego International Airport | [5 empty] | 32.7336 | -117.1831 | 13 | KSAN | 13 | 0
LAG | LAGSD | Laguna | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8454 | -116.4719 | 5030 | MLGC1 | 5737 | 4 mi NE
LLC | LLCSD | Lilac | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 33.2771 | -117.0693 | 1304 | VLCC1 | 1483 | 4 mi SE
LLD | LLDSD | Loveland | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8055 | -116.7879 | 1375 | ANEC1 | 2810 | 7 mi ENE
LPT | LPTSD | La Posta | CA | YES | 2011-07-13 | 2015-04-04 | ACTIVE | 32.7138 | -116.404 | 4000 | CMNC1 | 3268 | 4 mi W
LSV | LSVSD | Lawson Valley | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.7362 | -116.8224 | 1591 | ANEC1 | 2810 | 11 mi NE
MGR | MGRSD | Mussey Grade | CA | YES | 2010-01-25 | 2015-04-04 | ACTIVE | 32.9863 | -116.9081 | 1594 | KRNM | 1391 | 4 mi N
MGY | MGYSD | Mataguay | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.2233 | -116.6988 | 2803 | RCHC1 | 4415 | 12 mi E
MIG | MIGSD | San Miguel | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 32.6847 | -116.9801 | 500 | MIGC1 | 425 | 0
MOR | MORSD | Lake Morena | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.6884 | -116.5118 | 3085 | CMNC1 | 3268 | 4 mi NE
MPE | MPESD | Camp Elliot | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 32.8524 | -117.118 | 446 | MPEC1 | 539 | 1 mi ENE
MVN | MVNSD | Mission Valley North | CA | YES | 2011-10-03 | 2015-04-04 | ACTIVE | 32.781 | -117.138 | 206 | KMYF | 420 | 2 mi N
OLV | OLVSD | Olivenhain | CA | YES | 2011-08-02 | 2015-04-04 | ACTIVE | 33.0801 | -117.13 | 1167 | VLCC1 | 1483 | 13 mi NNE
OTY | OTYSD | Otay | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.7202 | -116.9278 | 863 | MIGC1 | 425 | 4 mi SW
PAM | PAMSD | Mt. Palomar | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.3521 | -116.8629 | 5483 | PAMC1 | 5486 | 0
PAU | PAUSD | Pauma Valley | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.3711 | -117.0789 | 411 | VLCC1 | 1483 | 10 mi SSE
PTM | PTMSD | Pala Temecula | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.4192 | -117.0819 | 1292 | VLCC1 | 1483 | 13 mi SSE
PVD | PVDSD | Palo Verde | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8132 | -116.7341 | 1841 | ANEC1 | 2810 | 4 mi ENE
RAM | RAMSD | Ramona | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 33.073 | -116.858 | 1514 | GOSC1 | 1835 | 1 mi NW
RBH | RBHSD | Rainbow Heights | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.414 | -117.126 | 1869 | SRUC1 | 1987 | 9 mi NW
RBV | RBVSD | Rainbow Valley | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 33.4012 | -117.1702 | 1087 | SRUC1 | 1987 | 9 mi NNW
RIN | RINSD | Rincon | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.2878 | -116.9564 | 1065 | VLCC1 | 1483 | 5 mi SW
RNB | RNBSD | Rainbow | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.4189 | -117.1441 | 1058 | SRUC1 | 1987 | 8 mi NW
RSF | RSFSD | Rancho Santa Fe | CA | YES | 2010-01-27 | 2015-04-04 | ACTIVE | 33.0333 | -117.1896 | 249 | KCRQ | 328 | 8 mi NW
SPP | SPPSD | Spangler Peak | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.9995 | -116.7885 | 1684 | GOSC1 | 1835 | 8 mi NW
SRH | SRHSD | Sunrise Hwy | CA | YES | 2010-01-23 | 2015-04-04 | ACTIVE | 32.8085 | -116.5083 | 4010 | CMNC1 | 3268 | 7 mi SSE
SYC | SYCSD | Sycamore Canyon | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.9143 | -117.0296 | 1038 | MPEC1 | 539 | 6 mi SW
TLK | TLKSD | Turner Lake | CA | YES | 2010-01-02 | 2015-04-04 | ACTIVE | 33.2262 | -117.0756 | 1249 | VLCC1 | 1483 | 4 mi E
VJS | VJSSD | Viejas | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.8456 | -116.7044 | 2345 | ANEC1 | 2810 | 2 mi ESE
VLC | VLCSD | Valley Center | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 33.2356 | -117.0068 | 1432 | VLCC1 | 1483 | 0
WAL | WALSD | West Alpine | CA | YES | 2010-08-25 | 2015-04-04 | ACTIVE | 32.8301 | -116.804 | 1554 | ANEC1 | 2810 | 8 mi E
WPT | WPTSD | West Potrero | CA | YES | 2010-08-10 | 2015-04-04 | ACTIVE | 32.6123 | -116.6133 | 2302 | POTC1 | 2345 | 1 mi SSE
WRB | WRBSD | West Rancho Bernardo | CA | YES | 2011-07-16 | 2015-04-04 | ACTIVE | 33.0311 | -117.122 | 749 | KNKX | 479 | 11 mi S
YSA | YSASD | Santa Ysabel North | CA | YES | 2010-08-30 | 2015-04-04 | ACTIVE | 33.1131 | -116.6718 | 3010 | PIHC1 | 3651 | 7 mi SSE

## WeatherIncidents
Incident | Start | End |  | Duration |  | STATIONS | [10 empty] | 2006 Norm
[5 empty] | VLCC1 | ANEC1 | GOSC1 | PIHC1 | SRUC1 | DENC1 | POTC1 | MIGC1 | Mean | Outage Wt | 2004-01-01
1 | 2005-03-30 | 2005-04-02 | Descanso | 4 | 41 | 42 | 33 | 42 | 41.1 | 48 | 44 | 30 | 40.1375 | 163.5545 | 2005-01-01 | 202.5263 | 0.47287
2 | 2005-11-14 | 2005-11-20 | PHC | 7 | 27 | 32 | 26 | 37 | 26 | 33 | 38 | 23 | 30.25 | 38.9718 | 2006-01-01 | 428.2884 | 1
3 | 2006-01-04 | 2006-01-07 | PHC | 4 | 38 | 40 |  | 42 | 34 | 39 | 52 | 18 | 37.5714 | 112.7197 | 2007-01-01 | 1545.6616 | 3.6089
4 | 2006-01-22 | 2006-01-24 | PHC | 3 | 33 | 39 | 30 | 39 | 35 | 44 | 48 | 20 | 36 | 89.7429 | 2008-01-01 | 493.0503 | 1.1512
5 | 2006-02-04 | 2006-02-09 | PHC | 6 | 41 | 31 | 29 | 37 | 34 | 37 | 41 | 19 | 33.625 | 63.588 | 2009-01-01 | 291.6587 | 0.68099
6 | 2006-10-26 | 2006-10-28 |  | 3 |  | 28 | 29 | 23 | 27 | 36 | 33 | 30 | 29.4286 | 34.5939 | 2010-01-01
7 | 2006-11-30 | 2006-12-07 | PHC | 8 |  | 39 | 37 | 36 | 46 | 37 | 44 | 30 | 38.4286 | 127.6439 | 2011-01-01 | 215.0727 | 0.50217
8 | 2007-01-05 | 2007-01-08 | Descanso | 4 |  | 42 | 41 | 41 | 48 | 42 | 48 | 27 | 41.2857 | 193.1968 | 2012-01-01
9 | 2007-03-01 | 2007-03-05 | PHC | 5 |  | 38 | 37 | 37 | 38 | 47 | 52 | 35 | 40.5714 | 174.1807 | 2013-01-01
10 | 2007-10-21 | 2007-10-24 |  | 4 | 52 | 59 | 55 | 56 | 39 | 60 | 69 | 40 | 53.75 | 1178.2841 | 2014-01-01 | 504.9692 | 1.179
11 | 2008-01-01 | 2008-01-03 |  | 3 | 56 | 32 | 44 | 37 | 42 | 42 | 38 | 32 | 40.375 | 169.2875 | 2015-01-01 | 318.2678 | 0.74312
12 | 2008-01-17 | 2008-01-19 |  | 3 | 48 | 27 | 19 | 34 | 28 | 46 | 34 | 16 | 31.5 | 46.7197 | 2016-01-01
13 | 2008-10-12 | 2008-10-15 |  | 4 | 39 | 34 | 23 | 51 | 28 | 45 | 41 | 22 | 35.375 | 81.9644
14 | 2008-11-06 | 2008-11-08 |  | 3 | 25 | 31 | 19 | 36 | 21 | 45 | 38 | 15 | 28.75 | 31.3509
15 | 2008-12-05 | 2008-12-07 |  | 3 | 75 | 22 | 27 | 27 | 25 | 30 | 36 | 22 | 33 | 58.0764
16 | 2008-12-09 | 2008-12-11 |  | 3 | 33 | 34 | 31 | 40 | 27 | 52 | 54 | 26 | 37.125 | 105.6513
17 | 2009-01-10 | 2009-01-13 |  | 4 | 42 | 66 | 35 | 53 | 31 | 50 | 51 | 25 | 44.125 | 291.6587
18 | 2011-01-22 | 2011-01-24 |  | 3 | 29 |  | 22 | 60 | 25 | 52 | 36 | 26 | 35.7143 | 86.0994
19 | 2011-02-02 | 2011-02-04 |  | 3 | 33 | 34 | 46 | 36 | 28 | 54 | 45 | 32 | 38.5 | 128.9734
20 | 2014-03-08 | 2014-03-10 |  | 3 | 33 | 38 | 33 | 51 | 26 | 31 | 31 | 29 | 34 | 67.1429
21 | 2014-04-30 | 2014-05-03 |  | 4 | 39 | 69 | 42 | 46 | 33 | 59 | 44 | 36 | 46 | 382.8247
22 | 2014-11-24 | 2014-11-26 |  | 3 | 27 | 56 | 27 | 33 | 27 | 38 | 32 | 21 | 32.625 | 55.0016
23 | 2015-01-23 | 2015-01-26 |  | 4 | 33 | 72 | 44 | 37 | 31 | 46 | 41 | 33 | 42.125 | 218.2102
24 | 2015-02-12 | 2015-02-14 |  | 3 | 40 | 50 | 43 | 34 | 29 | 35 | 34 | 29 | 36.75 | 100.0576
Total |  |  |  | 94
Fraction |  |  |  | 0.025125
Backgrounds |  |  |  | 54.1953

## Fires0815
SDG&E Related Wildland Incidents 2008 - 2015
File MGRA_DR-04_Q67_Amended
Record | Incident Type | Incident Name | System | Date/time Started | Responsible Agency | Fire Details | Suspected Cause - SDGE | Cause Class | Suspected Cause Details | Suspected Cause Status | Structure | Circuit | Fire Size | Fire Weather
5332 | SDGE Related Wildland | Buckman | Secondary | 2008-01-02 15:50 | CDF | Tree abrasion on secondary service, small spot in vegetation | Tree Contact with Power Lines | vegetation | Secondary, non-subject vegetation | Suspected | N/A | N/A | sm. spot | 1 | 2004-01-01 | Bin | Frequency
5333 | SDGE Related Wildland | Olive Hill | Distribution | 2008-01-16 10:35 | North Co. FPD | Eucalytus tree from across the roadway uprooted and fell across the street bringing down the 12 kV line. | Tree/Branch fell into Power Lines | vegetation | Compliant tree uprooted from across the street and took out power line. | Suspected | N/A | N/A | .25 acre | 0 | 2005-01-01 | 2004-01-01 | 0
5334 | SDGE Related Wildland | Elsa | Distribution | 2008-02-14 09:28 | San Diego City | Sparks from Capicitor ignited small patch of landscape vegetation | Equipment Failure on non-subject pole | equipment | Cap. Station ignited | Official | N/A | N/A | sm. spot | 0 | 2006-01-01 | 2005-01-01 | 0
5335 | SDGE Related Wildland | Descanso | Distribution | 2008-02-17 17:54 | CDF | Car/pole contact brought wire down, burned small spot of vegetation. | Car-Pole Contact | external | car/pole contact | Official | N/A | N/A | sm. spot | 0 | 2007-01-01 | 2006-01-01 | 0
5336 | SDGE Related Wildland | Sub base | Distribution | 2008-02-27 14:38 | Federal | Pole reported to be arcing causing small spot fire | Equipment Failure on non-subject pole | equipment | Pole equipment reported to be arcing | Official | N/A | N/A | sm. spot | 0 | 2008-01-01 | 2007-01-01 | 0
5337 | SDGE Related Wildland | Julian | Distribution | 2008-03-03 04:07 | CDF | Pine tree branch came in contact with conductor on circuit 221 | Tree Contact with Power Lines | vegetation | Pine tree branch came in contact with conductor on circuit 221 | Official | N/A | 221 | sm. spot | 0 | 2009-01-01 | 2008-01-01 | 0
5338 | SDGE Related Wildland | Claremont | Secondary | 2008-03-03 16:57 | San Diego City | Secondary pulled out of weatherhead and started side of building and small patch of ground fire | Equipment | equipment | Secondary failure | Official | N/A | N/A | sm. spot | 0 | 2010-01-01 | 2009-01-01 | 36
5342 | SDGE Related Wildland | Round Potrero | Distribution | 2008-04-08 04:35 | CDF | Wire down burning in brush about 2' diameter patch of vegetation | Power Line Down | equipment | Wire down | Official | N/A | N/A | sm. spot | 0 | 2011-01-01 | 2010-01-01 | 30
5343 | SDGE Related Wildland | Bonsall | Distribution | 2008-04-11 15:56 | CDF | Car/pole contact brought wires down causing small vegetation fire. | Car-Pole Contact | external | Car/pole contact brought wires down | Official | N/A | N/A | .25 acre | 0 | 2012-01-01 | 2011-01-01 | 32
5345 | SDGE Related Wildland | Jamul | Distribution | 2008-04-18 18:55 | SD Rural FPD | Private tree contractor caused tree into conductor causing small vegetation fire. | Private Tree Contactor | external | Private contractor caused wire down | Official | N/A | N/A | 0.5 Acre(s) | 0 | 2013-01-01 | 2012-01-01 | 25
5346 | SDGE Related Wildland | Sorrento Valley Blvd | Distribution | 2008-04-20 11:19 | San Diego City | Small fire at base of pole caused by faulty switch | Equipment Failure on non-subject pole | equipment | Faulty switch | Official | N/A | N/A | sm. spot | 0 | 2014-01-01 | 2013-01-01 | 23
5349 | SDGE Related Wildland | Guyman | Distribution | 2008-05-02 15:06 | San Diego City | Small spot of vegetation burned when fuse blew… | Equipment Failure on non-subject pole | equipment | Blown fuse | Official | N/A | N/A | sm. spot | 0 | 2015-01-01 | 2014-01-01 | 26
5350 | SDGE Related Wildland | Ash | Secondary | 2008-05-16 13:00 | CDF | 6 acres of mowed grass and small utility trailer burned when open wire secondary came to the ground | Power Line Down | equipment | Open wire secondary came down | Official | N/A | N/A | 6 Acre(s) | 0 | 2016-01-01 | 2015-01-01 | 27
5352 | SDGE Related Wildland | Poway | Distribution | 2008-05-16 13:00 | CDF | Transformer fire spread to vegetation. | Equipment Failure on Subject Pole | equipment | Transformer fire | Official | N/A | N/A | 18 Acre(s) | 0 |  | 2016-01-01 | 1
5355 | SDGE Related Wildland | Vista | Distribution | 2008-05-21 10:13 | Vista | Century plant came in contact w/conductor, burned tip of plant | Tree Contact with Power Lines | vegetation | Century Plant center stalk contact w/conductor | Official | N/A | N/A | 0 sq. ft. | 0 |  | More | 0
5356 | SDGE Related Wildland | Chula Vista | Dist/UG | 2008-05-24 23:30 | Chula Vista | Car/pad mounted transformer contact into vegetation, small spot of vegetation burned. | Car-Pole Contact | external | Car/pad mounted transformer contact | Official | N/A | N/A | sm. spot | 0
5360 | SDGE Related Wildland | Washington | Dist/UG | 2008-06-19 18:21 | Escondido | Equipment fault burned small 5x 20' spot of vegetation | Equipment Failure on non-subject pole | equipment | Equipment fault | Official | N/A | N/A | sm. spot | 0
5361 | SDGE Related Wildland | Dulin Rd. | Dist/UG | 2008-06-21 12:08 | Escondido | Vehicle vs. transformer, fire engulfed vehicle and ignited small amount of brush. | Car-Pole Contact | external | Car vs. transformer | Official | N/A | N/A | sm. spot | 0
5362 | SDGE Related Wildland | Jamul2 | Distribution | 2008-06-27 00:05 | CDF | Conductor down sm. spot | Power Line Down | equipment | Conductor down | Official | N/A | N/A | sm. spot | 0
5366 | SDGE Related Wildland | Bernardo Ave | Distribution | 2008-07-15 18:30 | Escondido | Vehicle accident causing wire down, igniting small vegetation fire | Car-Pole Contact | external | Car-pole contact brought wire down | Official | N/A | N/A | 0.5 Acre(s) | 0
5367 | SDGE Related Wildland | Oceanside | Distribution | 2008-07-31 12:54 | Oceanside | Contract employee vehicle ignited grass fire. | Vehicle exhaust | external | Pick-up truck off road, exhaust ignited vegetation… | Official | N/A | N/A | 20 Acre(s) | 0
5370 | SDGE Related Wildland | National City | Distribution | 2008-08-03 15:48 | National City | Wire down, very small spot of vegetation on landscape. | Power Line Down | equipment | Line down, unknown cause | Official | N/A | N/A | sm. spot | 0
5372 | SDGE Related Wildland | Kings Villa | Distribution | 2008-08-04 15:42 | CAL FIRE | Pvt. contractor equipment contact igniting small patch of grass in two locations. | Private contractor, roofer | external | Private contractor equipment contact | Official | N/A | N/A | sm. spot | 0
5373 | SDGE Related Wildland | Warners | Distribution | 2008-08-07 16:00 | CAL FIRE | Bird into wire, landed on ground igniting very small spot of vegetation | Foreign Object in Line | external | Bird into wire | Official | N/A | N/A | sm. spot | 0
5376 | SDGE Related Wildland | Chula Vista | Secondary | 2008-08-18 15:55 | Chula Vista | Small spot of vegetation burned when telco line came in contact with secondary service. | Other Utility Contact | other | Telco line came in contact with secondary | Official | N/A | N/A | sm. spot | 0
5378 | SDGE Related Wildland | Canal Rd. | Distribution | 2008-08-20 23:45 | San Pasqual Fire | Wire down by burned small patch of vegetation | Wire down, gun shot | external | Wire shot down by unknown subject. | Official | N/A | N/A | sm. spot | 0
5384 | SDGE Related Wildland | Rice Cyn | Secondary | 2008-09-03 07:00 |  | Small fire below secondary service to well pump | Arcing Power Line | equipment | Arcing secondary | Official | N/A | N/A | sm. spot | 0
5387 | SDGE Related Wildland | blossom Valley | Distribution | 2008-09-13 13:32 | Lakeside | Dump truck hit pole and knocked it over burning small spot of vegetation | Car-Pole Contact | external | Dump truck into pole | Official | N/A | N/A | sm. spot | 0
5385 | SDGE Related Wildland | Sycuan | Distribution | 2008-09-14 10:27 | Sycuan FD | Bird contact w/conductor on circuit 283, burned very small spot of vegetation. | Foreign Object in Line | external | Bird into conductor | Official | N/A | N/A | sm. spot | 0
5382 | SDGE Related Wildland | western trails | Secondary | 2008-09-15 17:43 | El Cajon | Contact with tree causing some scorching/smoldering in tree. | Tree Contact with Power Lines | vegetation | Tree contact with secondary service | Official | N/A | N/A | sm. spot | 0
5388 | SDGE Related Wildland | Cedar Lane | Distribution | 2008-09-18 16:03 | Escondido | Mylar balloons into conductors causing very small spot | Foreign Object in Line | external | Mylar balloon into conductor | Official | N/A | N/A | sm. spot | 0
5386 | SDGE Related Wildland | Lyons Valley | Distribution | 2008-09-21 05:45 | CAL FIRE | Small fire resulting from bird into conductor on circuit 157 | Foreign Object in Line | external | Bird into conductor | Official | N/A | N/A | sm. spot | 0
5390 | SDGE Related Wildland | Old River Road | Distribution | 2008-10-14 10:30 | no response | Small spot of vegetation burned as a result of grinding activities | Grinding | external | Grinding | Official | N/A | N/A | sm. spot | 1
5392 | SDGE Related Wildland | Deluz | Secondary | 2008-10-14 10:30 | Deluz VFD | Tree uprooted and fell bringing down line and causing small 1/4 acre brush fire. | Tree/Branch fell into Power Lines | vegetation | Tree contact | Official | N/A | N/A | .25 acre | 1
5398 | SDGE Related Wildland | Sycamore | Distribution | 2008-11-02 17:00 | North Co. FPD | Car/pole contact caused fuse to ignite vegetation | Equipment Failure on Subject Pole | external | Lightning arrestor blew when circuit re-energized from a car/pole contact | Official | N/A | N/A | sm. spot | 0
5403 | SDGE Related Wildland | Acorn Patch | Distribution | 2008-11-14 | Poway | Queen Palm made contact w/12 kV line burning small 4 x 8' patch of grass at base. | Tree Contact with Power Lines | vegetation | Tree contact | Official | N/A | N/A | sm. spot | 0
5405 | SDGE Related Wildland | Cuca | Dist/UG | 2009-01-20 07:25 | San Diego City | Transformer fire small spot | Underground failure | equipment | UG transformer failure | Official | N/A | N/A | sm. spot | 0
5406 | SDGE Related Wildland | Highland Valley | Distribution | 2009-02-02 20:53 | Poway | Car/pole contact resulting in wire down and small brush fire | Car-Pole Contact | external | Car/pole contact resulting in wire down and small brush fire. | Official | N/A | N/A | sm. spot | 0
5411 | SDGE Related Wildland | Japanese Mesa | Distribution | 2009-05-04 13:30 | Orange Co. Fire | Faulty switch (SCE equipment) caused small brush fire (our service territory) |  | equipment | SCE switch faulted causing vegetation fire | Official | N/A | N/A | 1 Acre(s) | 0
5417 | SDGE Related Wildland | Landis | Secondary | 2009-06-08 16:15 | San Diego City | Failed tree guard sleeve causing burning of individual palm fronds, no additional acreage. | Tree Contact w/secondary lines | vegetation | Palm frond contact with secondary conductor | Official | N/A | N/A | sm. spot | 0
5418 | SDGE Related Wildland | Escondido | Distribution | 2009-06-13 03:45 | Escondido | Small fire from blown lightning arrestor | Equip. Failure non-subject pole | equipment | small fire from blown lightning arrestor |  | N/A | N/A | sm. spot | 0
5420 | SDGE Related Wildland | decease | Distribution | 2009-06-23 19:46 | CAL FIRE | Tree branch fell across 12 kv line was smoldering when FD arrived | Tree/Branch fell into P. Lines | vegetation | Tree contact | Official | N/A | N/A | sm. spot | 0
5422 | SDGE Related Wildland | Kearny Villa | Distribution | 2009-06-27 09:30 | San Diego City | Cracked insulator caused very small spot fire next to pole on circuit 771. | Equip. Failure non-subject pole | equipment | Equipment failure | Official | N/A | N/A | sm. spot | 0
5421 | SDGE Related Wildland | why 80 | Secondary | 2009-07-06 14:04 | CAL FIRE | PS & neutral squeeze on rubbed together causing small 20 x 20' spot fire | Equip. Failure non-subject pole | equipment | Equipment failure | Official | N/A | N/A | sm. spot | 0
5423 | SDGE Related Wildland | Highway 80 | Secondary | 2009-07-06 15:03 | USFS | Secondary wiring bad insulation burning 20' x 20' spot of vegetation | Arcing Power Line (secondary) | equipment | Arcing secondary caused 20' x 20' spot of vegetation | Official | N/A | N/A | sm. spot | 0
5424 | SDGE Related Wildland | Valley Center | Distribution | 2009-07-14 13:53 | CAL FIRE | Crew work caused blown fuse resulting in small fire | Contractor related | external | Crew work caused fuse to blow | Official | N/A | N/A | sm. spot | 0
5425 | SDGE Related Wildland | Valley Center | Distribution | 2009-07-22 21:45 | CAL FIRE | Failed sleeve on conductor caused a small spot and burned fence. | Contractor related | equipment | Failed sleeve on conductor | Official | N/A | N/A | sm. spot | 0
5426 | SDGE Related Wildland | Miguel | Other | 2009-07-23 14:30 | CAL FIRE | SDGE road grader apparently clipped rock and sparked 1 acre grass fire. | Other, company road grader | external | Road work equipment | Official | N/A | N/A | 1 Acre(s) | 0
5427 | SDGE Related Wildland | Terrell | Distribution | 2009-07-26 15:00 | Escondido | Lightning arrestor exploded and burn small patch of grass | Equip. Failure non-subject pole | equipment | Equipment failure | Official | N/A | N/A | sm. spot | 0
5431 | SDGE Related Wildland | del Obisbo | Distribution | 2009-08-05 04:23 | Orange Co. Fire | 20' x 20' spot of vegetation burned when a cutout feeding a capacitor bank burned. | Equip. Failure non-subject pole | equipment | Equipment failure | Official | N/A | N/A | sm. spot | 0
5432 | SDGE Related Wildland | Hedy | Distribution | 2009-08-06 | CAL FIRE | Tree contact w/conductor, tree was smoldering on ground, no additional vegetation involved… | Tree/Branch fell into P. Lines | vegetation | Tree contact | Official | N/A | N/A | sm. spot | 0
5433 | SDGE Related Wildland | el Cajon | Distribution | 2009-08-24 20:37 | El Cajon | Blown lightning arrestor caused small spot of vegetation 30' x 20' | Equip. Failure non-subject pole | equipment | Blown lightning arrestor | Suspected | N/A | N/A | sm. spot | 0
5434 | SDGE Related Wildland | Mt. Helix | Secondary | 2009-08-26 11:37 | San Miguel FPD | Secondary connection, sparks to ground igniting adjacent vegetation, small spot | Equip. Failure non-subject pole | equipment | Aluminum squeeze-on connector failed, | Official | N/A | N/A | sm. spot | 0
5436 | SDGE Related Wildland | Rancho Santa Fe | Distribution | 2009-08-26 14:15 | Rancho Santa Fe | Boom contact w/conductor burning tree branches | Employee Related | external | Equipment contact w/conductor | Official | N/A | N/A | 0 sq. ft. | 0
5435 | SDGE Related Wildland | Lawson Valley | Distribution | 2009-08-28 14:39 | CAL FIRE | Car/pole bringing pole conductor into vegetation igniting a 1 acre brush fire. | Car-Pole Contact | external | Car/pole wire down | Official | N/A | N/A | 1 Acre(s) | 0
5437 | SDGE Related Wildland | Cuyamaca | Distribution | 2009-09-10 | El Cajon | OH capacitor failed sending a fault to ground igniting very small spot fire | Equip. Failure non-subject pole | equipment | OH capacitor failed sending a fault to ground | Official | N/A | N/A | sm. spot | 0
5438 | SDGE Related Wildland | Lakeside | Secondary | 2009-09-14 14:30 | Lakeside | Pvt. Resident tree contact limbs burn |  | vegetation | Private tree felling into secondary | Official | N/A | N/A | 0 sq. ft. | 0
5440 | SDGE Related Wildland | Spring Valley | Distribution | 2009-09-27 | San Miguel FPD | Mylar Balloon into 12 kV igniting small spot fire. | Foreign Object in Line | external | Mylar Balloon into 12 kV | Official | N/A | N/A | sm. spot | 0
5441 | SDGE Related Wildland | Silverbrook | Secondary | 2009-09-29 13:47 | El Cajon | Tree failure into secondary wire, no fire spread only charring of branches | Tree/Branch fell into P. Lines | vegetation | Tree failure | Official | N/A | N/A | 0 sq. ft. | 0
5442 | SDGE Related Wildland | Beach Cities | Distribution | 2009-09-29 22:58 | San Diego City | Wire failure burned small spot of vegetation | Power Line Down | equipment | Wire failure | Official | N/A | N/A | sm. spot | 0
5443 | SDGE Related Wildland | Angel | Distribution | 2009-10-08 | CAL FIRE | Insulator tracked over to cross-arm igniting and sending sparks to ground burning small spot | Equip. Failure non-subject pole | equipment | Insulator tracking | Official | N/A | N/A | sm. spot | 0
5446 | SDGE Related Wildland | White Lilac/ | Distribution | 2009-10-27 |  | Bucket contact with conductor, resulting in small 3' diameter spot of grass to burn. | Employee Related | external | Equipment contact w/conductor | Official | N/A | N/A | sm. spot | 0
5447 | SDGE Related Wildland | Ortega | Distribution | 2009-11-16 11:45 | Orange Co. Fire | Pole knocked down by private grading operation igniting vegetation fire. | Tractor-pole contact | external | Private tractor | Official | N/A | N/A | 145 Acre(s) | 0
5448 | SDGE Related Wildland | Escondido | Distribution | 2009-11-18 19:51 | San Marcos | Tree broke out and struck conductor causing about 1/10 acre of adjoining vegetation to burn. | Tree/Branch fell into P. Lines | vegetation | Tree contact | Official | N/A | N/A | sm. spot | 0
5449 | SDGE Related Wildland | Jamul | Distribution | 2009-11-22 08:15 | CAL FIRE | Wire down from gunshot, very small spot of vegetation no additional damage. | Power Line Down | external | Power line down due to gunshot | Official | N/A | N/A | sm. spot | 0
5452 | SDGE Related Wildland | Silver Shadow | Distribution | 2009-12-28 | San Marcos | Sleeve failure wire down burning only brush in contact with conductor, no fire spread | Power Line Down | equipment | Sleeve failure | Official | N/A | N/A | sm. spot | 0
6004 | SDGE Related Wildland | Grandview | Distribution | 2010-01-06 12:00 | La Mesa | Tree contact small spot of vegetation. | Other, private tree contractor | vegetation | Tree contact | Final |  | 371 | 10 sq. ft. | 0
5453 | SDGE Related Wildland | Grandview | Distribution | 2010-01-06 09:00 | San Miguel FPD | Wire down, burned small 10' spot of vegetation | Other, private tree contractor | external | Private tree contractor tree contact | Official | N/A | N/A | sm. spot | 0
6005 | SDGE Related Wildland | Palomar Mtn. | Distribution | 2010-01-12 12:00 | USFS | Very small spot 1' x 1' from tree contact | Other, private tree contractor | external | Private tree contractor tree contact | Final | P219059 | 214 | 1 sq. ft. | 0
5454 | SDGE Related Wildland | Palomar Mtn. | Distribution | 2010-01-12 | no response | Tree trimmer dropped tree/branch into wire burning a very small 6' spot of vegetation, | Power Line Down | external | Private tree contractor tree contact | Official | N/A | N/A | sm. spot | 0
6008 | SDGE Caused Other | Serena | Distribution | 2010-01-19 12:00 | Lakeside | Tree contact with wire during high wind event, burn mark on conductor no vegetation | Tree Contact with Power Lines | vegetation | Tree contact | Final | P370735 | 1138 | 0 sq. ft. | 0
6009 | SDGE Related Wildland | Nordica | Distribution | 2010-01-25 12:00 | San Diego City | Small 2' x 2' spot fire of grass, no additional fire spread | Power Line Down | equipment | Wire down | Final |  | 80 | 4 sq. ft. | 0
5455 | SDGE Related Wildland | Nordica | Distribution | 2010-01-25 08:31 | San Diego City | Circuit 80 wire down mid-span burned 2 x 2' patch of lawn (grass). | Power Line Down | equipment | Wire down mid-span | Official | N/A | N/A | sm. spot | 0
6011 | SDGE Related Wildland | Molino | Distribution | 2010-02-05 12:00 | Orange Co. Fire | Small spot base of broken pole, lightening in the area | Equipment Failure on Non-Subject Pole | equipment | Broken pole, lightning in the area…root cause undetermined | Final |  |  | 100 sq. ft. | 0
6013 | SDGE Related Wildland | Robinhood | Distribution | 2010-03-14 12:00 | San Marcos | Fire Department extinguished small spot fire in citrus tree. | Other Utility Contact | equipment | Tree contact w/communications line | Final | P211743 | 1091 | 25 sq. ft. | 0
6016 | SDGE Related Wildland | Spring Valley | Distribution | 2010-03-19 12:00 | San Miguel FPD | Broken pole caused conductors to fall to ground contacting vegetation burning small spot. | Equipment Failure/ Pole | equipment | Broken pole caused conductors t fall to ground | Final | P171425 | 731 | 100 sq. ft. | 0
6017 | SDGE Related Wildland | Otay 1 | Distribution | 2010-04-11 12:00 | San Diego City | Wire down in brush, likely related to shooting, 4 acres of vegetation burned | other, wire shot down | external | Wire down shooting | Final |  | 260 | 4 Acre(s) | 0
6018 | SDGE Related Wildland | Mission Viejo | Distribution | 2010-05-02 12:00 | Orange Co. Fire | Small spot of vegetation | Equipment Failure/ Pole | equipment | Failure of lightning arrestor pothead fuse | Under Investigation | P128076 | 556 | 100 sq. ft. | 0
6019 | SDGE Related Wildland | Bonsall | Distribution | 2010-05-03 09:55 | CAL FIRE | mid-span break in distribution phase igniting small grass fire, 50' x 50'. | Foreign Object in Line | equipment | Remote control plane contact w/conductor | Under Investigation | P217236 | 239 | 2500 Acre(s) | 0
6020 | SDGE Related Wildland | Otay Mesa | Distribution | 2010-05-09 17:09 | San Diego City FD | Car into pole which brought wire down igniting small brush fire | Car-Pole Contact | external | Vehicle accident | Final | P82413 | 334 | 100 sq. ft. | 0
6022 | SDGE Related Wildland | Pala | Distribution | 2010-05-15 10:11 | CAL FIRE | Private helicopter contact w/system and brought down one pole and two long spans causing fire approximately 20' x 300' | Power Line Down | external | Third party contact (helicopter) | Under Investigation | Unknown | 908 | 6000 sq. ft. | 0
6026 | SDGE Related Wildland | Woodland | Distribution | 2010-05-23 02:30 | San Marcos | Pole fell due to rot and conductors came in contact with vegetation igniting a 900 sq. ft. spot | Power Line Down | equipment | Pole failure | Final | P131083 | 183 | 900 sq. ft. | 0
6027 | SDGE Related Wildland | San Clemente | Distribution | 2010-05-25 09:47 | Orange Co. Fire | Fault caused a parallel groove clamp connector failure igniting small spot of vegetation approx.. 20' x 60' | Connector failure | equipment | Equipment failure | Final | P226940 | 200 | 1200 sq. ft. | 0
6028 | SDGE Related Wildland | Vesper | Distribution | 2010-05-28 16:52 | CAL FIRE | 10' x 10' spot of vegetation at base of pole | Connector failure | equipment | Equipment failure | Final | P113693 | 909 | 100 sq. ft. | 0
6034 | SDGE Related Wildland | Twin Peaks | Distribution | 2010-06-20 12:00 | Poway | Capacitor failure sparks fell into vehicle bed burning bed and small spot of vegetation | Equipment Failure/ Pole | equipment | Fault in capacitor | Under Investigation |  | 178 | 10 sq. ft. | 0
6035 | SDGE Related Wildland | Reche | Distribution | 2010-06-23 19:01 | North Co. FPD | Small vegetation fire at base of pole (10' x 10' spot) | Connector failure | equipment | Faulty compression connection | Final | P116701 | 230 | 100 sq. ft. | 0
6023 | SDGE Related Wildland | South Mission Road Secondary | Secondary | 2010-06-28 15:54 | North Co. FPD | Secondary wire fell into dry vegetation resulting in spot fire. Non HRFA. | Connector failure | equipment | Failure of Cu to Al connector. | Final | P5111840 | 233 | 225 sq. ft. | 0
6037 | SDGE Related Wildland | Fallbrook | Distribution | 2010-07-13 14:20 | North Co. FPD | Cap Station explosion resulting in 30 x 50' vegetation fire | Equipment Failure/ Pole | equipment | Fault in Capacitor Station | Under Investigation | Cap Sta 522-138 | 522 | 150 sq. ft. | 0
6041 | SDGE Related Wildland | Naranca | Distribution | 2010-08-03 16:00 | El Cajon | Lightening arrestors blew igniting fire on ground | Equipment Failure/ Pole | equipment | 3 lightening arrestors were found blown | Final | P574095 | 418 | 4 Acre(s) | 0
6046 | SDGE Related Wildland | Robertson | Secondary | 2010-08-15 21:00 | CAL FIRE | Arcs from secondary connection burned 3' x 3' patch of vegetation | Connector failure | equipment | Secondary sleeve failure (Copper to Aluminum) | Final | Sta. #972700 | 972 | 10 sq. ft. | 0
6048 | SDGE Related Wildland | Riverview | Distribution | 2010-08-20 16:00 | Lakeside | failed secondary connector sparked and fell to the ground igniting fire. | Equipment Failure/ Pole | equipment | failed secondary connector. | Final | P78226 | 242 | 50 sq. ft. | 0
6052 | SDGE Related Wildland | Manana | Distribution | 2010-09-27 11:00 | San Diego City FD | Branch from tree under the sagging line was burned but did not ignite any ground fire. | Tree Contact with Power Lines | vegetation | Tree contact | Final | P732612 | LJ3 | 0 sq. ft. | 0
6053 | SDGE Related Wildland | Mission | Distribution | 2010-09-27 13:00 | San Marcos FD | Vegetation fire at base of pole. | Phase Overload | equipment | Equipment failure gang switch | Under Investigation | P130959 | 183 | 1 Acre(s) | 0
6054 | SDGE Related Wildland | Ridgeton | Distribution | 2010-10-01 12:30 | Lakeside | small vegetation fire at base of pole. | Equipment Failure/ Pole | equipment | Capacitor failure on pole. | Final |  | 245 | 1 Acre(s) | 0
6057 | SDGE Caused Other | Via Madonna | Distribution | 2010-10-13 08:16 | Orange Co. Fire | Capacitor failure, equipment fire only. Damage to capacitor and fuse holder. | Equipment Failure/ Pole | equipment | Capacitor failure | Under Investigation | Cap.Sta. #196-948 | 196 | 0 sq. ft. | 0
6058 | SDGE Related Wildland | Hwy 94 | Distribution | 2010-11-09 17:00 | CAL FIRE | One 12kv phase dropped to ground igniting 4 separate vegetation fires. | Power Line Down | external | Possible gun shot severed line. | Under Investigation | P171405 | 75 | sm. spot | 0
6059 | SDGE Related Wildland | Friars | Distribution | 2010-11-30 07:30 | San Diego City FD | at 10'x10' spot fire ignited by faulted switch | Equipment | external | Bird contact causing transformer/arrestor igniting multiple small fires. | Final | P579675 | 38 | 100 sq. ft. | 0
6062 | SDGE Related Wildland | Santa Fe | Distribution | 2010-12-23 01:30 | Rancho Santa Fe | small spot fire on landscaping bark | Tree/Branch fell into Power Lines | vegetation | Tree contact | Final | P319114 | 1001 | 1 sq. ft. | 0
6064 | SDGE Related Wildland | Valley Center | Distribution | 2011-01-23 07:04 | CAL FIRE | Wire down caused by mid-span slap in high wind igniting small 50' by 50' spot | Power Line Down | equipment | Mid-span slap caused break, wire down, small spot | Final | P312924 | 217 | 2500 sq. ft. | 1
6068 | SDGE Related Wildland | Willow Glen | Distribution | 2011-03-31 10:42 | San Miguel FPD | Fuse tripped throwing sparks into dry vegetation at base of pole. Fire burned a 5' x 5' diameter | Equipment | equipment | Equipment failure | Final | P10933 | 524 | 25 sq. ft. | 0
6069 | SDGE Related Wildland | Pala Mesa | Distribution | 2011-04-02 14:00 | North Co. FPD | Contractor brought old and new line together on pole energized igniting small 10 x 10' spot fire in grass. | Power Line Down | equipment | Conductor contact | Under Investigation | Z219397 | c-230 | 100 sq. ft. | 0
6073 | SDGE Related Wildland | Gila | Distribution | 2011-05-02 10:04 | San Diego City FD | An umbrella blew up into the conductors igniting very small spot of grass | Foreign Object in Line | external | Third party contact (umbrella) | Final | p834462 | 276 | 4 sq. ft. | 0
6074 | SDGE Related Wildland | Williams ranch | Secondary | 2011-05-04 12:00 | CAL FIRE | Tree rubbed against secondary causing sparks igniting small patches of grass | Tree Contact w/secondary lines | vegetation | Tree contact w/secondary service | Final | P418015 | 227 | 100 sq. ft. | 0
6076 | SDGE Related Wildland | Barnett | Distribution | 2011-05-12 16:10 | CAL FIRE | Bird(s) contact causing transformer explosion igniting multiple small fires | Foreign Object in Line | external | Bird contact | Final | P513191 | 235 | .25 acre | 0
6082 | SDGE Related Wildland | Oceanside | Distribution | 2011-05-17 11:30 | Oceanside | A palm frond contact blew fuse igniting material w/no further spread. | Tree/Branch fell into Power Lines | vegetation | Palm frond boot contact with conductor | Final | P512362 | 487 | 16 sq. ft. | 0
6079 | SDGE Related Wildland | Wilshire | Distribution | 2011-05-24 12:15 | Oceanside | Automatic sleeve failed which dropped line to ground igniting fire. | Equipment | equipment | Equipment failure | Final | P114085 | 486 | 10 sq. ft. | 0
6083 | SDGE Related Wildland | Donovan | Distribution | 2011-05-30 14:42 | San Diego City | Bad aluminum to copper connections 1/2 acre of vegetation burned as a result of this fire | Connector failure | equipment | Bad aluminum to copper connections | Under Investigation | P31617 | 534 | 0.5 Acre(s) | 0
6080 | SDGE Related Wildland | Calle Dulcinea | Distribution | 2011-05-31 09:58 | Orange Co. Fire | Surge caused two groove clamps to melt and drop to ground igniting vegetation. | Equipment | equipment | fault current | Final | P25327 | 200 | 5 Acre(s) | 0
6084 | SDGE Related Wildland | Century Plant | Distribution | 2011-06-02 17:20 | CAL FIRE | Century Plant into primary conductor bringing wire to ground igniting vegetation fire burning approx.. 1/2 acre. | Tree Contact with Power Lines | vegetation | Century Plant made contact w/primary | Final | P514661-P514662 | 350 | 0.5 Acre(s) | 0
6085 | SDGE Related Wildland | Richfield | Secondary | 2011-06-02 12:00 | El Cajon | Crew made contact with a neutral causing sparks igniting a palm tree stub and a small patch of grass. | Employee Related | external | SDGE employee conductor contact |  |  | R11 | 16 sq. ft. | 0
6086 | SDGE Related Wildland | Encinitas | Distribution | 2011-06-02 16:42 | Encinitas | Small spot fire (20 sq. ft.) ignited when wire came down due to mylar balloon contact. | Foreign Object in Line | external | Mylar balloon contact brought primary down igniting small grass fire. | Final |  | 289 | 20 sq. ft. | 0
6090 | SDGE Related Wildland | Del Mar | Distribution | 2011-06-29 14:10 | San Diego City | Tree w/girdled roots approx.. 40' from conductors failed fell into conductor causing a fault igniting small spot of vegetation. | Tree/Branch fell into Power Lines | vegetation | Third party tree contact | Final | Z12315 | 63 | 100 sq. ft. | 0
6091 | SDGE Related Wildland | Otay | Distribution | 2011-07-13 16:04 | San Diego City | Melted metal dripping from faulty secondary connection ignited small spot of grass | Connector failure | equipment | Faulty secondary | Final | P164412 | 460 | 110 Acre(s) | 0
6100 | SDGE Related Wildland | Bell Fire | Distribution | 2011-08-24 09:00 | CAL FIRE | SDGE contractor generator exhaust caused 20 acre fire | Contractor Related | external | Hot equipment exhaust | Final | P43915 | 448 | 20 Acre(s) | 0
6101 | SDGE Related Wildland | Cristianitos | Distribution | 2011-08-25 | Orange Co. Fire | Conductor contact during construction causing small fire | Arcing Power Line | external | Conductor contact | Final | P224436 | 339 | 80 Acre(s) | 0
6102 | SDGE Related Wildland | Pala | Distribution | 2011-08-29 11:00 | CAL FIRE | 223 acre fire cause by vehicle (compact car) into a pole | Vehicle versus power pole | external | Third party vehicle contact | Under Investigation |  | 249 | 223 Acre(s) | 0
6104 | SDGE Related Wildland | Los Coches | Secondary | 2011-09-07 12:45 | Lakeside | A secondary service contact with a tree, faulting and causing a small ground fire | tree contact | vegetation | tree contact |  |  | 245 | 1 Acre(s) | 0
6107 | SDGE Related Wildland | Sunrise EP42 Incident | Other | 2011-09-19 14:13 | CAL FIRE | Fire area of one (1) sq. ft. in wildland grass. Caused by contactor working with a backhoe | Contractor Related | external | Road work equipment | Final | SRPL EP42 | N/A | 1 sq. ft. | 0
6108 | SDGE Related Wildland | Bonsall | Distribution | 2011-10-10 | CAL FIRE | One square foot of grass was burned with sparks fell from a pole from a burned out jumper. | Jumper Failure | equipment | Equipment failure | Final | P115579 | 233 | 1 sq. ft. | 0
6112 | SDGE Related Wildland | Hwy 395 Fire | Distribution | 2011-10-18 15:29 | CAL FIRE | Burned out jumper caused the grass near the pole to burn. | Burned out Jumper | equipment | Equipment failure | Final | P210429 | 354 | 25 sq. ft. | 0
6113 | SDGE Related Wildland | Willow Glen | Distribution | 2011-11-01 04:02 | CAL FIRE | Wire down causing 1/2 acre fire | Power Line Down | equipment | Conductor failure cause unknown | Under Investigation | 73664 | 91 | 0.5 Acre(s) | 0
6114 | SDGE Related Wildland | Maranatha | Distribution | 2011-11-09 16:30 | CAL FIRE | 5 acre fire caused by failed switch | Equipment | equipment | Faulty switch | Final | 218479 | 1100 | 5 Acre(s) | 0
6116 | SDGE Related Wildland | Wing | Distribution | 2011-11-29 11:00 | El Cajon | small spot fire at base of pole. | Connector failure | equipment | Equipment failure (connector) | Final | P675828 | 392 | 1 sq. ft. | 0
6121 | SDGE Related Wildland | Mellmanor Drive | Distribution | 2012-03-09 16:42 | La Mesa/Heartland | Blown fuse caused 25 sq. ft. veg to burn | Equipment Failure/ Pole | equipment | Blown fuse | Final | JP578639 | 406 | 25 sq. ft. | 0
6122 | SDGE Related Wildland | Creek | Distribution | 2012-03-20 19:41 | San Diego City FD | Small 2 x2' spot along downed powerline, fire went out when line was de-energized…no additional spread. | Arcing Power Line | equipment | Wire down | Final | P471603 | 921 | 4 sq. ft. | 0
6123 | SDGE Related Wildland | Millard | Distribution | 2012-04-09 16:39 | San Miguel FPD | Bird contacted wire burning a 10' x 10' circle | Animal Contact | external | Bird into wire. | Final | P271547 | 75 | 20 sq. ft. | 0
6126 | SDGE Related Wildland | Kalmia | Distribution | 2012-05-14 12:00 | Escondido | wire fell to ground in backyard of residence landing on cut grass. | Contractor Related | external | contractor, tree trimmer | Final |  | ES4 | 25 sq. ft. | 0
6129 | SDGE Related Wildland | Mother Grundy | Distribution | 2012-05-23 11:00 | CAL FIRE | Lightning arrestors flashed igniting small 30' x 30' spot of grass | Equipment | equipment | Lightning arrester failure | Final | P474526 | 67 | 900 sq. ft. | 0
6127 | SDGE Related Wildland | C.V.Lotus & Spruce | Distribution | 2012-05-24 17:22 | Chula Vista | mylar balloons into a pole mounted transformer. Burning material fell to the ground igniting the uncut wild grass | Foreign Object in Line | external | Mylar Balloons | Final |  | 152 | 300 sq. ft. | 0
6128 | SDGE Related Wildland | Tierra Del Sol | Distribution | 2012-05-28 13:20 | CAL FIRE | Vehicle into pole causing 3 acre fire | Car-Pole Contact | external | Third party vehicle contact | Final |  | 445 | 3 Acre(s) | 0
6131 | SDGE Related Wildland | Imperial Beach Circuit 531 | Distribution | 2012-06-02 11:57 | Chula Vista | Mylar Balloon into conductor causing small fire | Foreign Object in Line | external |  | Under Investigation |  | 531 | 250 sq. ft. | 0
6130 | SDGE Related Wildland | Otay Circuit 155 | Distribution | 2012-06-03 06:04 | Chula Vista | Fire caused by line down ignited the wild grass under the lines. Fire estimated at 300-600 sq. ft. | Foreign Object in Line | equipment |  | Under Investigation |  | 155 | 300 sq. ft. | 0
6134 | SDGE Related Wildland | Highland Valley | Distribution | 2012-07-07 13:15 | Poway | Mylar Balloon into cable pole causing sparks igniting small fire | Foreign Object in Line | external | Mylar balloon contact w/conductor | Under Investigation | unknown | 175 | .25 acre | 0
6135 | SDGE Related Wildland | Jacumba | Distribution | 2012-07-17 22:29 | CAL FIRE | Single wire came down into dry grass along roadside igniting fire. | Power Line Down | equipment | wire failed at pole | Final | P42421 | 444 | 100 sq. ft. | 0
6136 | SDGE Related Wildland | Lakeside - Westhill Rd | Distribution | 2012-08-06 18:00 | Lakeside | Fire burn limited to approximately 80 sq ft of wild grass near the base of pole. | Equipment | equipment | Failed cutout | Under Investigation | P471725 |  | 80 sq. ft. | 0
6138 | SDGE Related Wildland | OC - San Juan | Distribution | 2012-08-10 08:35 | Orange Co. Fire | 800 Sq. Ft. of wildland grass (20x40) spot near the base of the pole. OCFD on scene upon ETS arrival. | Equipment | equipment | blown porcelain lightning arrestor. | Under Investigation | P28736 | 1073 | 800 sq. ft. | 0
6141 | SDGE Related Wildland | Willow | Distribution | 2012-09-14 08:30 | Lakeside | Grounded 'guy' wire contacted single phase which produced spark. | Equipment | equipment | Equipment (Guy wire) | Final | P971573 | 248 | 100 sq. ft. | 0
6142 | SDGE Related Wildland | Kimball Valley | Distribution | 2012-09-20 19:45 | CAL FIRE | 30 sq ft spot of wildland grass caused by wire down. Extinguished by home owner | Power Line Down | external | Apparent gunshot | Under Investigation | p219739 | 971 | 30 sq. ft. | 0
5459 |  | Kimball Valley | Distribution | 2012-09-20 | CAL FIRE | Possible gunshot caused small fire | Power Line Down |  | Suspected gunshot damage | Suspected | N/A | N/A | 435.6 sq. ft. | 0
6143 | SDGE Related Wildland | Kalbaugh | Distribution | 2012-09-28 12:00 | CAL FIRE | Failed squeeze connector caused 4 acre fire. | Connector failure | equipment | Suspected to be started by deteriorated squeeze-on connector | Under Investigation | P311451 | 972 | 4 Acre(s) | 0
6144 | SDGE Related Wildland | Jamul | Distribution | 2012-09-28 12:15 | CAL FIRE | Truck snagged a Telco drop igniting a 1 acre fire. | Prvt vehicle contact w/telco causing wire slap | external | Third party contact | Under Investigation |  | 524 | 1 Acre(s) | 0
6145 | SDGE Related Wildland | Vista Sage | Distribution | 2012-10-12 12:00 | CAL FIRE | 10'x10' spot fire between P74503 and P171926. | Foreign Object in Line | external | Mylar balloon | Final | P74583 | 75 | 100 sq. ft. | 0
6150 | SDGE Related Wildland | Quarry | Distribution | 2012-10-29 12:30 | CAL FIRE | Drilling rig contacted telco lines causing wire down igniting a small (1/2 acre) wildland fire. | Prvt vehicle contact w/telco causing arc | external | Third party contact | Under Investigation | P208578 | 354 | 20000 sq. ft. | 0
6151 | SDGE Related Wildland | Bancroft & Campo | Distribution | 2012-11-02 14:20 | San Miguel FPD | Capacitor failed causing hot material to fall and ignite cut, dry grass at base of pole. | Equipment Failure/ Pole | equipment | Equipment failure (Capacitor) | Under Investigation | P373785 | CMP1 | 400 sq. ft. | 0
6152 | SDGE Related Wildland | Jacumba #2 | Distribution | 2012-11-08 02:20 | CAL FIRE | fire fell to ground igniting a small area of vegetation. No significant spread. | Power Line Down | equipment | Wire failure near dead-end shoe. | Final | P42421 | 444 | 6 sq. ft. | 0
6155 | SDGE Related Wildland | Montecito | Distribution | 2012-11-24 14:00 | CAL FIRE | Two lightning arrestors failed and ignited a 1/4 acre grass fire.. | Equipment | equipment | Equipment failure | Under Investigation | P13291 | 972 | .25 acre | 0
6157 | SDGE Related Wildland | La Canada | Distribution | 2013-02-07 06:20 | North Co. FPD | Sleeve failure wire down, two small 1 foot spots of smoldering oak leaves. | Connector failure | equipment | Bad connector | Final | P2113150 | 1235 | 2 sq. ft. | 0
6161 | SDGE Related Wildland | Wildcat | Distribution | 2013-03-12 15:53 | CAL FIRE | Cross-arm failure wire to ground igniting and burning small spot of vegetation about 50 sq. sq. ft.. | Equipment Failure Cross-arm | equipment | Cross-arm failed | Under Investigation | P221270 | 973 | 50 sq. ft. | 0
6162 | SDGE Related Wildland | Paradise - at Hwy 125 & Hwy 54 | Distribution | 2013-03-24 15:15 | San Miguel FPD | Burning oil from pole mounted capacitor bank dropped to the ground igniting the wild grass at pole base. | Equipment Failure/ Pole | equipment | Equipment failure (Capacitor) | Under Investigation | P163271 | 326 | 200 sq. ft. | 0
6163 | SDGE Related Wildland | In Line Switch | Trans/Dist. | 2013-04-03 22:45 | North Co. FPD | Inline switch failed all on its own, no other help. | Equipment | equipment | In line switch failure. | Final | P108385 | 230 | 100 sq. ft. | 0
6165 | SDGE Related Wildland | Monserate | Distribution | 2013-04-14 14:00 | North Co. FPD | Wire down on circuit 230 burned small spot of grass 1' x1' spot. | Power Line Down | equipment | Wire down under investigation | Under Investigation | P610497 | 230 | 1 sq. ft. | 0
6166 | SDGE Related Wildland | Walnut Dr - Ramona | Distribution | 2013-04-17 14:30 | CAL FIRE | Fire est. 1/4+ acre of wild and cut grass along roadway and onto a field. | Equipment | equipment | Faulty connector | Under Investigation | 116073 | 972 | .25 acre | 0
6169 | SDGE Related Wildland | Wood Valley | Distribution | 2013-04-28 15:15 | CAL FIRE | Mylar balloon caused phase to phase and resulted in blown fuse. | Foreign Object in Line | external | Mylar Balloon | Under Investigation | p774713 | 524 | 90 sq. ft. | 0
6167 | SDGE Related Wildland | Broadway | Distribution | 2013-05-01 12:40 | San Diego City | Suspected aluminum connector failure | Connector failure | equipment | Connector failure | Under Investigation | P471445 | 322-170 | 100 sq. ft. | 0
6168 | SDGE Related Wildland | Pala Greenhouse | Distribution | 2013-05-02 15:00 | North Co. FPD | Mid-span break wire down two sm. fires | Equipment | equipment | Equipment failure | Under Investigation | 114174 | 1234 | 10 sq. ft. | 0
6171 | SDGE Related Wildland | Mapleview | Distribution | 2013-05-12 12:00 | Lakeside | Small grass fire (2 acres) from blown insulator | Blown Insulator | equipment | Equipment failure (insulators) | Under Investigation | P476188 | 242 | 2 Acre(s) | 0
6174 | SDGE Related Wildland | W. Lilac Rd. | Distribution | 2013-06-14 19:00 | CAL FIRE | Failed lightning arrestor causing 1/2 acre fire | Equipment Failure/ Pole | equipment | Equipment failure (arrestor) | Under Investigation | 616868 | 350 | 0.5 Acre(s) | 0
6178 | SDGE Related Wildland | Skyway Montezuma | Distribution | 2013-06-27 10:20 | CAL FIRE | Blown lightning arrestor, shards landed outside PRC circle | Equipment | equipment | Unknown reason for failure | Final |  | 211 | 2 Acre(s) | 0
6180 | SDGE Related Wildland | Pendleton Tracking | Distribution | 2013-06-28 10:30 | Camp Pendleton FD | Bird nest ignited, tracking | Tracking | external | Cause uncertain | Final |  | 300 | 37 Acre(s) | 0
6179 | SDGE Related Wildland | Main Street IC | Distribution | 2013-07-03 12:00 | Chula Vista | Commercial vehicle contact causing 25 acre fire. | Prvt vehicle contact w/telco causing wire slap | external | Third Party contact | Under Investigation | P108483 | 463 | 25 Acre(s) | 0
6181 | SDGE Related Wildland | Lamar | Distribution | 2013-07-07 12:37 | San Miguel FPD/CALFIRE | Small spot fire occurred when fuse to capacitor bank blew | Equipment | equipment | Capacitor | Under Investigation | Z371294 | 732 | 10 sq. ft. | 0
6191 | SDGE Related Wildland | San Ysidro - Dairymart Rd | Distribution | 2013-08-11 19:20 | San Diego City | Fire limited to 4 sq ft of dried grass at base of pole. | Equipment Failure/ Pole | equipment | Failure of a pole mounted switch | Under Investigation | P160918 | 443 | 2 sq. ft. | 0
6189 | SDGE Related Wildland | Sierra Rojo | Distribution | 2013-08-14 12:30 | CAL FIRE | 2 wires down and burned some canopy in the river bottom. Additionally, a fuse blew at other location which caused an additional 10x10 spot fire at P518263. | Contractor Related | external | Suspected contractor work nearby | Under Investigation | P518263 | 1021 | 100 sq. ft. | 0
6192 | SDGE Related Wildland | Tomahawk | Distribution | 2013-08-29 15:00 | San Diego City | Mylar balloons igniting (2) very small grass patches in a park strip. FD put out fires. | Foreign Object in Line | external | Mylar Balloons | Under Investigation | P2356070881 | 492 | 6 sq. ft. | 0
6193 | SDGE Related Wildland | Hollyhock | Distribution | 2013-08-31 11:15 | National City | Car/pole contact causing a very small spot fire. | Car-Pole Contact | external | Car/pole contact caused conductor contact with tree. | Under Investigation | P201164 | 42-30 | 10 sq. ft. | 0
6196 | SDGE Related Wildland | Lilac | Distribution | 2013-09-13 06:45 | CAL FIRE | Wire came down and ignited brush. | Other | equipment | under investigation. | Under Investigation | P410321 | 350 | .25 acre | 0
6198 | SDGE Related Wildland | Rincon - Rocky | Distribution | 2013-10-05 05:04 | CAL FIRE | Fire burned approximately 1/4 to 1/3 (0.25 - 0.3) acres of vegetation. Believed to be related to ground wire wooden shield | Equipment | equipment | Ground wire fault | Under Investigation | 717128 | 216 | .25 acre | 0
6201 | SDGE Related Wildland | Imperial Trolley | Secondary | 2013-10-06 04:06 | San Diego City FD | Fire burned approx.. 250 sq ft of vegetation in and along a drainage ditch that ran parallel to the trolley tracks. | Other | equipment | Secondary wire down unknown cause. | Under Investigation |  | 323 | 250 sq. ft. | 0
6199 | SDGE Related Wildland | Hwy 78 | Distribution | 2013-10-07 03:58 | Oceanside | Car pole contact shearing pole off at base. | Car-Pole Contact | external | Third party contact | Final | P211926 | 192 | 400 sq. ft. | 0
6200 | SDGE Related Wildland | Egg Ranch | Distribution | 2013-10-08 11:14 | CAL FIRE | Wire down | Equipment | equipment | Loose jumper | Under Investigation | P17727 | 222 | 2 Acre(s) | 0
6203 | SDGE Related Wildland | Juniper | Secondary | 2013-11-16 05:00 | San Miguel FPD/CALFIRE | Small spot of veg burned in flowerbed and a little charring on the juniper tree through which the wire ran. | Arcing Power Line (secondary) | equipment | Bad tree guard | Final | P672107 | 94 | 100 sq. ft. | 0
6206 | SDGE Related Wildland | Via Puerta Del Sol | Distribution | 2013-12-27 15:00 | CAL FIRE | Failed lightning arrestor caused hot material to drop onto vegetation which ignited a small 80 sq. ft. fire. | Equipment | equipment | Equipment failure (lightning arrestor) | Under Investigation | P716665 | 233 | 80 sq. ft. | 0
6207 | SDGE Related Wildland | Escondido | Distribution | 2014-01-01 18:45 | Escondido | Small spot fire at base of distribution pole. | Equipment | equipment | Bad secondary connector failed at pole. | Under Investigation | P11112 | 514 | 1 sq. ft. | 0
6209 | SDGE Related Wildland | Mtn. Meadow | Distribution | 2014-03-05 09:49 | CAL FIRE | Wire down, several 'small spot fires'- | Power Line Down | equipment | Unknown root cause possible connector or broken wire. | Under Investigation | P515262 | 353 | sm. spot | 0
6210 | SDGE Related Wildland | Sumatra Ln - Bullock Dr | Distribution | 2014-04-15 06:20 | San Diego City FD | Fire burned approximately 250 sq. ft., roughly a 10x25 ft. area of short wild grass. | Employee Related | external | Work activities caused conductor contact | Under Investigation | Z180434 | 324 | 250 sq. ft. | 0
6213 | SDGE Related Wildland | Rincon | Distribution | 2014-04-28 16:20 | CAL FIRE | Car/pole caused small fire | Car-Pole Contact | external | Car pole contact | Under Investigation | P812595 | 214 | 100 sq. ft. | 0
6214 | SDGE Related Wildland | Highway 76 | Distribution | 2014-04-28 13:30 | CAL FIRE | Small spot fire burned when wire came down and ignited vegetation | Power Line Down | equipment | Sleeve failure caused wire to come down and ignite adjacent grass. | Under Investigation | P215546 | 214 | 100 sq. ft. | 0
6215 | SDGE Related Wildland | Via Monserate | Distribution | 2014-04-29 10:05 | CAL FIRE | Trash truck dumpster lift into conductor bringing it down starting a small to medium strip of vegetation to burn. | Car-Pole Contact | external | Car/pole caused wire down | Final | P213051 | 233 | 500 sq. ft. | 0
6216 | SDGE Related Wildland | Canyon Crest | Distribution | 2014-04-29 01:40 | Escondido | Car/pole contact ignited small spot of vegetation | Car-Pole Contact | external | Car/pole contact ignited small spot of vegetation. | Final | P316707 | 455 | 100 sq. ft. | 0
6217 | SDGE Related Wildland | Paradise | Distribution | 2014-04-29 16:49 | San Diego City | Tree broke out during strong winds bringing down two wires causing a small 5' x 60' spot fire | Tree/Branch fell into Power Lines | vegetation | Tree into power lines | Final | P476600 | 323 | 300 sq. ft. | 0
6218 | SDGE Related Wildland | Los Coches | Distribution | 2014-05-01 06:48 | CAL FIRE | Telco line into conductor, fire burned approx.. 4 acres | Foreign Object contact w/conductor | other | Third party contact | Under Investigation | P372465 | 242 | 4 Acre(s) | 1
6220 | SDGE Related Wildland | Dulzura | Distribution | 2014-05-13 09:00 | CAL FIRE | Vegetation fire est. size of 0.33 acre burned grass. | Power Line Down | equipment | Suspected wire slap | Under Investigation | P177622 | 157 | .33 acre | 0
6221 | SDGE Related Wildland | Lawson (a.k.a. Hillary Fire) | Secondary | 2014-05-13 08:35 | CAL FIRE | 0.25 acre vegetation fire under a large willow tree. | Tree Contact w/secondary lines | vegetation | Tree branch rubbing | Under Investigation | P274777 | 524 | .25 acre | 0
6222 | SDGE Related Wildland |  | Distribution | 2014-05-19 18:30 | CAL FIRE | single phase landed in grass and started fire. | Power Line Down | other | Third party equipment contact (telco) | Under Investigation | P211709 | 597 | 1 Acre(s) | 0
6224 | SDGE Related Wildland | Via De La Valle | Distribution | 2014-05-28 15:50 | San Diego City FD | Car-pole contact. | Car-Pole Contact | external |  | Final | P313226 | 66 | 5 sq. ft. | 0
6225 | SDGE Related Wildland | Timber | Distribution | 2014-05-31 11:30 | CAL FIRE | Timber fallers had dropped tree into wires contacting vegetation and causing fire. | Power Line Down | external | Third party contact | Final | P219919 | 214 | 2 Acre(s) | 0
6223 | SDGE Related Wildland | Creelman | Trans/Dist. | 2014-06-04 09:30 | CAL FIRE | SDGE Contractor contact during construction causing sm. fire | Contractor Related | external | SDGE contractor work | Under Investigation | Z416592 | TL637 Cir. 970 | 600 sq. ft. | 0
6226 | SDGE Related Wildland | Otay | Distribution | 2014-06-17 15:30 | San Diego City FD | Switch failure caused sm. fire | Equipment | equipment |  | Under Investigation | 192047 | 1201 | 100 sq. ft. | 0
6227 | SDGE Related Wildland | Jamacha | Secondary | 2014-07-04 12:00 | CAL FIRE | 2' diameter branch from a California Pepper tree rubbed on secondary causing sparks igniting sparse weeds approximately 2 square sq. ft. in size. | Tree Contact w/secondary lines | vegetation | Tree contact w/power lines | Final | P471597 | 96 | 4 sq. ft. | 0
6228 | SDGE Related Wildland | Highland Valley | Distribution | 2014-07-06 11:30 | CAL FIRE | The fire was about 50' x 100' in sparse grass adjacent to a road and vineyard. | Blown Fuse | external | Blown fuse caused by bird contact | Final | P319081 | 972 | 500 sq. ft. | 0
6229 | SDGE Related Wildland | Dehesa | Distribution | 2014-07-22 10:25 | CAL FIRE | 2 Small spot. Guy wire caused fault between 12Kv and underbuilt telco line resulting in a fault and arc. | Car-Pole Contact | external | Third party contact | Final | P276288 | 283 | 50 sq. ft. | 0
6232 | SDGE Related Wildland | Creelman2 | Distribution | 2014-08-28 12:52 | CAL FIRE | Contractor work caused spark igniting fire. | Contractor Related | external | Contractor work, contact w/energized conductor. | Under Investigation | Z416585 | 970 | .25 acre | 0
6233 | SDGE Related Wildland | Twin Oaks | Distribution | 2014-09-02 11:15 | San Marcos | 100 sq. ft. wild grass fire | Foreign Object contact w/conductor | external | Mylar balloon | Under Investigation | P219744 | 599 | 100 sq. ft. | 0
6235 | SDGE Related Wildland | Nelson Way | Distribution | 2014-09-11 11:56 | CAL FIRE | Transformer failure, lid blew off and sparks ignited small 10' x 10' spot fire in adjacent grass. | Equipment | equipment | Failure of transformer, blew lid off and ignited adjacent ground fuels | Under Investigation | p619040 | 350 | 100 sq. ft. | 0
6236 | SDGE Related Wildland | Skyline | Distribution | 2014-09-13 20:30 | CAL FIRE | Broken secondary wire mid-span. ETS Weldy in possession of wire. Kelley Gallagher investigating for CALFIRE. | Power Line Down | equipment | Possible gunshot, nothing specific in area to contribute. | Under Investigation | P106190 | 157 | 0.75 Acre(s) | 0
6237 | SDGE Related Wildland | Fan Palm | Distribution | 2014-09-15 12:53 | San Miguel FPD | Mexican Fan Palm grew into and severed SSC causing fault and fire in palm. | Tree Contact w/secondary lines | vegetation |  | Under Investigation | P162177 | 162 | 0 sq. ft. | 0
6238 | SDGE Related Wildland | Highway 78 | Distribution | 2014-09-24 19:45 | CAL FIRE | bird flew into 4kV conductor igniting bird and sending sparks and bird to ground igniting surrounding vegetation (approx.. 30' x 30'). | Animal Contact | external | Bird into wire | Final | P169791 | RA1 | 900 sq. ft. | 0
6240 | SDGE Related Wildland | Barona | Distribution | 2014-10-11 04:00 | CAL FIRE | 20'x20' spot fire in light grass. | Foreign Object contact w/conductor | external | Unknown foreign object | Under Investigation | P222837 | 974 | 400 sq. ft. | 0
6241 | SDGE Related Wildland | Lake Jennings (MVU-Old) | Distribution | 2014-11-19 09:30 | CAL FIRE | Third party tractor made contact with power pole igniting 2 separate small spot fires totaling approximately 1/2 acre. | Tractor-pole contact | external | Third party contact | Final | P272232 | 246 | 0.5 Acre(s) | 0
6243 | SDGE Related Wildland | High Ridge Rd | Distribution | 2015-02-11 15:30 | Lakeside | Italian Cypress rubbing on secondary service line caused fire on ground and in branches of the cypress | Tree Contact w/secondary lines | vegetation | No tree guard was in use but will be now. | Final | P237657 | 240 | 50 sq. ft. | 0

## Fires0407
SDGE Related Fire Cause Data 2005-2007 | [8 empty] | 2004-01-01 | Bin | Frequency | Fire Types |  | Fire Weather | Background
[9 empty] | 2005-01-01 | 2004-01-01 | 0 | Equipment | 142 | 3 | 3.5678
Date Started | Incident # | Incident Name | District Location | System | Acres | Cause Related Comments | Cause Class | Fire Weather | 2006-01-01 | 2005-01-01 | 19 | Vegetation | 44 | 5 | 1.1055
[9 empty] | 2007-01-01 | 2006-01-01 | 25 | Other | 4 | 2 | 0.1005
2004-03-16 | 5136 | Eastgate Mall | Beach Cities | D | 0.1 | Faulty switch, sm. spot grass | equipment | 0 | 2008-01-01 | 2007-01-01 | 27 | External | 99 | 1 | 2.4874
2004-03-19 | 5137 | Black Canyon | Ramona | D | 0.25 | Tree down/wire down, sm. brush fire | vegetation | 0 | 2009-01-01 | 2008-01-01 | 19
2004-04-16 | 5140 | Bonita | Metro | T/D | 0.1 | Smoking limbs/cut power/fire out | vegetation | 0 | 2010-01-01 | 2009-01-01 | 0 | Total | 289 | 11 | 7.2612
2004-04-28 | 5141 | Rainbow Glen | Northeast | D | 10 | Dozer/tree/wire down, 10 acre fire | external | 0 | 2011-01-01 | 2010-01-01 | 0
2004-05-06 | 5145 | Del Mar | North Coast | D | 0.1 | Wire down, smoldering branch | equipment | 0 | 2012-01-01 | 2011-01-01 | 0
2004-05-24 | 5147 | Sleepy | Ramona | D | 2 | Boom conductor contact/ 2 acre fire | external | 0 | 2013-01-01 | 2012-01-01 | 0
2004-05-25 | 5148 | Bostonia | Eastern | D | 0.1 | Wire down/burned palm, no add. veg. | equipment | 0 | 2014-01-01 | 2013-01-01 | 0
2004-07-01 | 5153 | Old Highway 80 | Eastern | D | 0.1 | Dump truck/wire down, sm. spot veg. | external | 0 | 2015-01-01 | 2014-01-01 | 0
2004-07-07 | 5157 | El Monte | Eastern | D | 0.5 | Forklift into wire/line surge, 1/2 acre | external | 0 | 2016-01-01 | 2015-01-01 | 0
2004-07-17 | 5160 | Roselle | Beach Cities | T/D | 0.1 | Wire down, sm. spot veg. | equipment | 0 |  | 2016-01-01 | 0
2004-07-20 | 5161 | Vista del Valle | Eastern | D | 0.1 | Wire down, sm. spot veg. | equipment | 0 |  | More | 0
2004-09-05 | 5187 | Harmony | Northeast | D | 2 | Wire down, 2 acre brush fire | equipment | 0
2004-09-07 | 5191 | La Valle Plateada | North Coast | D | 0.1 | Tree contact, wire down, sm. spots | vegetation | 0
2004-09-21 | 5193 | Sycamore | Northeast | D | 0.1 | Wire down, sm. spot | equipment | 0
2004-11-01 | 5197 | Sunnyside | Metro | D | 0.1 | Trash truck/pole/wire down, tree fire | external | 0 | 2005-01-01 | 25
2004-11-21 | 5198 | Mountain Meadow | Northeast | D | 0.1 | Wire down, sm. spot | equipment | 0 | 2006-01-01 | 27
2004-12-16 | 5199 | Wynola | Ramona | D | 5 | Hvy wind, wire down, 5 acre fire | equipment | 0 | 2007-01-01 | 19
2004-12-16 | 5200 | Power | Moutain Empire | D | 0.1 | Hvy wind, wire down, sm. spot | equipment | 0 | 2008-01-01 | 36
2004-12-17 | 5201 | Green Valley | Ramona | D | 0.1 | Hvy wind, wire down, 2 sm. spots | equipment | 0 | 2009-01-01 | 30
2005-02-19 | 5069 | Willow Glen | Northeast | D | 0.1 | Wind storm, wire down, sm. spot veg. | equipment | 0 | 2010-01-01 | 32
2005-04-16 | 5071 | Canyon Road | Northeast | D | 0.1 | Transformer fire, sm. spot veg. | equipment | 0 | 2011-01-01 | 25
2005-04-21 | 5067 | Rice Canyon | Northeast | D | 1 | SDGE Crew, flashover, sm. brush fire | external | 0 | 2012-01-01 | 23
2005-04-28 | 5072 | Laguna Niguel | Orange County | D | 0.1 | Tree branch through wire, sm. spot | vegetation | 0 | 2013-01-01 | 26
2005-05-03 | 5062 | Otay Lakes | Metro | D | 0.1 | Pvt. Contractor, wire down, small spot | external | 0 | 2014-01-01 | 27
2005-05-11 | 5073 | Cypress Lane | Northeast | D | 0.1 | Aluminum connector melt, sm. spot | equipment | 0 | 2015-01-01 | 1
2005-05-19 | 5074 | Valley Center Road | Northeast | D | 0.1 | Bird in transformer, sm. spot veg. | external | 0
2005-06-12 | 5077 | Fruitvale | Northeast | D | 0.1 | Mylar balloon/wire down, sm. spot | external | 0
2005-06-21 | 5079 | Viejas Grade | Moutain Empire | D | 0.1 | Tree branch/line down, sm. spot | equipment | 0
2005-07-12 | 5093 | Mejillones | Beach Cities | D | 0.1 | Transformer fire, sm. spot veg. | equipment | 0
2005-07-21 | 5061 | Pine Hills | Ramona | D | 0.1 | Blown fuse, 2' diameter spot veg. | equipment | 0
2005-08-25 | 5065 | Lago Lindo | North Coast | D | 0.1 | Pvt. Contractor hit line, sm. spot veg. | external | 0
2005-08-28 | 5110 | vivero | Eastern | D | 0.1 | Wire down, sm. spot landscape veg. | equipment | 0
2005-09-13 | 5112 | Le Conte | Orange County | D | 0.5 | Guy wire/phase contact, 1/2 acre fire | equipment | 0
2005-09-14 | 5116 | Highland Valley | Northeast | D | 0.5 | Bird in wire/arc, 1/2 acre veg. fire | external | 0
2005-09-15 | 5118 | Borrego Springs | Ramona | D | 2 | Wire down, 2 acre brush fire | equipment | 0
2005-09-19 | 5119 | Lemon Grove | Eastern | D | 0.1 | Transformer fault, landscape veg. fire | equipment | 0
2005-10-04 | 5126 | Sunshine Summit | Ramona | D | 0.1 | Bird/wire/fell to ground, no veg | external | 0
2005-10-06 | 5063 | Via De Montana | Eastern | D | 0.1 | Pvt. Contractor, dig in 6' x 10' spot | external | 0
2005-10-13 | 5131 | Carlsbad Circuit 779 | North Coast | D | 0.1 | Veh./UG transformer, sm. spot veg. | external | 0
2005-10-26 | 5132 | Bernardo Center | Northeast | D | 0.1 | Bird/wire/fell to ground, sm. spot veg. | external | 0
2005-10-29 | 5133 | Millar | Eastern | D | 0.25 | Faulty hot tap clp/wire down, 1/4 acre | equipment | 0
2005-11-01 | 5064 | Buena | North Coast | D | 0.1 | Landscapers, wire down, small spot | external | 0
2005-11-29 | 5134 | Stage Coach | Northeast | D | 0.5 | Tree uprooted/wires down, 1/2 acre | vegetation | 0
2005-12-11 | 5059 | Jewel Valley | Moutain Empire | D | 0.25 | Wire down, 1/4 acre brush fire | equipment | 0
2006-02-07 | 5048 | Laguna Niguel | Orange County | D | 1 | Tree in compliance, fell from heavy winds into conductor, taking line down and burning small landscape hedge | vegetation | 1
2006-02-22 | 5051 | Kirkham | Northeast | D | 0.1 | Backhoe wire down small spot veg. | external | 0
2006-02-27 | 5052 | Steffy | Ramona | D | 0.1 | Bird nest, sm. twig burned/fell to grnd. | external | 0
2006-03-10 | 5054 | Harrison Park | Ramona | D | 0.1 | Snow load, wire down, 3 sm. spots | external | 0
2006-04-09 | 5055 | Bradley Incident | Eastern | D | 0.1 | Faulty switch, 4' x 6' spot | equipment | 0
2006-05-10 | 5177 | Castle Crest | Northeast | D | 0.1 | Grove wkr contact w/wire, sm. spot | external | 0
2006-05-29 | 5178 | Borrego Valley | Ramona | D | 0.1 | Wire down, sm. veg. fire, 3 sm. trees | equipment | 0
2006-06-10 | 5176 | Sage | Northeast | D | 0.1 | Dozer/wire down, 15' spot grass | external | 0
2006-06-14 | 5174 | Gayle Street | Metro | D | 0.1 | Tree contact, sm. patch grass | vegetation | 0
2006-06-17 | 5173 | Hillsdale | Eastern | D | 0.1 | Faulty switch, sm. spot grass | equipment | 0
2006-06-18 | 5172 | Laguna Niguel | Orange County | D | 0.5 | Bird contact/ 1/2 acre fire | external | 0
2006-06-20 | 5170 | La Mesa Mylar | Eastern | D | 0.1 | Mylar balloon into wire, sm. grass fire | external | 0
2006-06-27 | 5185 | Alta Vista | Northeast | D | 0.1 | Tree contact, wire down, 15'x15' spot | vegetation | 0
2006-06-29 | 5181 | Mussey Grade | Ramona | D | 0.1 | Tree contact, smoldering branch only | vegetation | 0
2006-07-04 | 5180 | Betsworth | Northeast | D | 0.1 | Pole fire, 3' patch grass base of pole | equipment | 0
2006-07-04 | 5221 | Betsworth | Northeast | D | 0.1 | Small spot at base of pole | equipment | 0
2006-07-08 | 5220 | Lilac | Northeast | D | 0.5 | Crew work wire contact, 1/2 acre | external | 0
2006-07-28 | 5213 | Olive | Northeast | D | 0.25 | Wire down, sm. veg. fire | equipment | 0
2006-08-03 | 5214 | Oceanside | North Coast | D | 0.1 | Equip. failure, sm. grass fire @ base | equipment | 0
2006-08-08 | 5210 | Lowe Chaparral | Northeast | D | 0.1 | Transformer fire, sm. spot veg. | equipment | 0
2006-09-20 | 5231 | Japatul Valley | Moutain Empire | D | 0.1 | Car/pole contact, sm. spot veg. | external | 0
2006-09-26 | 5238 | Bernardo Road | Northeast | D | 0.1 | Cap station arc, 5'x10' spot veg. | equipment | 0
2006-10-17 | 5239 | Pequito | Orange County | D | 0.1 | Palm frond contact, no sprd to veg. | vegetation | 0
2006-10-27 | 5242 | boulder creek | Moutain Empire | T/D | 2 | Hvy. wind, wire down, 2 acre fire | equipment | 1
2006-10-29 | 5246 | Warmlands | North Coast | D | 0.1 | Sm. spot base of pole from blown fuse | equipment | 0
2006-11-30 | 5250 | Open, San Ysabel | Ramona | D | 290 | Hvy. wind, wire down, 290 acre fire | equipment | 1
2006-12-25 | 5252 | Deluz 12 25 06 | Northeast | D | 0.1 | Wire down, sm. spot veg. | equipment | 0
2007-01-14 | 5256 | Almayo | Beach Cities | D | 0.1 | Equip. failure, sm. grass fire @ base | equipment | 0
2007-02-04 | 5258 | Miramar Nursery | Beach Cities | D | 0.1 | Undetermined specific cause | equipment | 0
2007-02-05 | 5260 | Miramar Nursery2 | Beach Cities | D | 0.25 | Undetermined specific cause | equipment | 0
2007-03-03 | 5261 | Jamul | Eastern | D | 0.1 | Tree split out in high winds and knocked down power lines. | vegetation | 1
2007-03-22 | 5263 | Avery Parkway | Orange County | D | 0.1 | Blown capacitor ignited small patch of vegetation | equipment | 0
2007-04-01 | 5264 | Beaver Hollow | Eastern | D | 0.1 | Cross-arm failure brought line down | equipment | 0
2007-04-11 | 5267 | Warmlands | North Coast | D | 0.1 | wire down from tree contact | vegetation | 0
2007-06-12 | 5282 | Cole Grade | Northeast | D | 0.1 | Century plant center stalk in contact w/conductor | vegetation | 0
2007-06-13 | 5283 | Black | Ramona | D | 0.25 | Wire down on circuit 220 between P610412 & P610413 | equipment | 0
2007-07-02 | 5292 | Washingtonia | Northeast | D | 0.25 | Delivery truck came in contact with bundle of cable swinging it up into the 12 kV line | external | 0
2007-07-05 | 5291 | Highway 76 | Northeast | D | 0.1 | Bad squeeze-on brought 12 kV line down igniting two small patches of vegetation | equipment | 0
2007-07-21 | 5290 | Guejito | Northeast | D | 0.1 | Third party caused, car into pole resulting in small vegetation fire | external | 0
2007-08-08 | 5302 | Bonita | Metro | D | 0.1 | Wire down, tree branch into power line | vegetation | 0
2007-08-13 | 5305 | Mina de Oro | Northeast | S/D | 10 | Tree fell into S service bringing down wire (s) | vegetation | 0
2007-08-14 | 5306 | Date | Metro | D | 0.1 | conductor tree contact burned palm tree frond on 4 kV circuit | vegetation | 0
2007-08-28 | 5310 | Main St. CV | Metro | D | 0.1 | Blown fuse, small spot of veg. | equipment | 0
2007-09-24 | 5318 | Barrett Lake | Moutain Empire | D | 12 | Squeeze on sleeve failed bringing down conductor, igniting fire(s) | equipment | 0
2007-10-21 | 5327 | Guejito | Northeast | D | Unknown | Investigation in progress - possible communications wire contacting electric conductor in high winds | other | 1
2007-10-22 | 5325 | Rice | Northeast | D | 9472 | Investigation in progress - possible portion of a compliant tree breaking and contacting conductors in high winds | vegetation | 1

## FiresFW
Fires During Fire Weather
SDGE Related Fire Cause Data 2004-2007
Date Started | Incident # | Incident Name | District Location | System | Acres | Cause Related Comments | Cause Class | Fire Weather
2006-02-07 | 5048 | Laguna Niguel | Orange County | D | 1 | Tree in compliance, fell from heavy winds into conductor, taking line down and burning small landscape hedge | vegetation | 1
2006-10-27 | 5242 | boulder creek | Moutain Empire | T/D | 2 | Hvy. wind, wire down, 2 acre fire | equipment | 1
2006-11-30 | 5250 | Open, San Ysabel | Ramona | D | 290 | Hvy. wind, wire down, 290 acre fire | equipment | 1
2007-03-03 | 5261 | Jamul | Eastern | D | 0.1 | Tree split out in high winds and knocked down power lines. | vegetation | 1
2007-10-21 | 5327 | Guejito | Northeast | D | Unknown | Investigation in progress - possible communications wire contacting electric conductor in high winds | other | 1
2007-10-22 | 5325 | Rice | Northeast | D | 9472 | Investigation in progress - possible portion of a compliant tree breaking and contacting conductors in high winds | vegetation | 1
SDG&E Related Wildland Incidents 2008 - 2015
File MGRA_DR-04_Q67_Amended
Record | Incident Type | Incident Name | System | Date/time Started | Responsible Agency | Fire Details | Suspected Cause - SDGE | Cause Class | Suspected Cause Details | Suspected Cause Status | Structure | Circuit | Fire Size | Fire Weather
5332 | SDGE Related Wildland | Buckman | Secondary | 2008-01-02 15:50 | CDF | Tree abrasion on secondary service, small spot in vegetation | Tree Contact with Power Lines | vegetation | Secondary, non-subject vegetation | Suspected | N/A | N/A | sm. spot | 1
5390 | SDGE Related Wildland | Old River Road | Distribution | 2008-10-14 10:30 | no response | Small spot of vegetation burned as a result of grinding activities | Grinding | external | Grinding | Official | N/A | N/A | sm. spot | 1
5392 | SDGE Related Wildland | Deluz | Secondary | 2008-10-14 10:30 | Deluz VFD | Tree uprooted and fell bringing down line and causing small 1/4 acre brush fire. | Tree/Branch fell into Power Lines | vegetation | Tree contact | Official | N/A | N/A | .25 acre | 1
6064 | SDGE Related Wildland | Valley Center | Distribution | 2011-01-23 07:04 | CAL FIRE | Wire down caused by mid-span slap in high wind igniting small 50' by 50' spot | Power Line Down | equipment | Mid-span slap caused break, wire down, small spot | Final | P312924 | 217 | 2500 sq. ft. | 1
6218 | SDGE Related Wildland | Los Coches | Distribution | 2014-05-01 06:48 | CAL FIRE | Telco line into conductor, fire burned approx.. 4 acres | Foreign Object contact w/conductor | other | Third party contact | Under Investigation | P372465 | 242 | 4 Acre(s) | 1

## Decision Matrix
| Study Segment | [8 empty] | Results |  | Ignition Risk | [12 empty] | Impact
[12 empty] | Environment |  |  |  |  | System
| A | A1 | A2 | B | B1 | B2 | B3 | B4 | C | D | E | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 17 | 18 | Totals | Shutoff | DistTotal
| 96% | [10 empty] | 8% | 12% | 10% | 12% | 10% | 3% | 3% | 2% | 2% | 2% | 2% | 4% | 5% | 12% | 3% | 3% | 3% | 96% | 4% | 3480.2222
ndx | Ckt | Op Dist | Sub | Section Start | Section End | Section End | Section End | Section End | Dist (Mi) | Score | Rank | Zone | Wind | Tree | Fuel | Fire Ign. Risk | Cap | Exp Fuse | SWs | Cond | Trans (All) | HR Trans | DOC Rank | Rel Hist | Value Risk | Crit Svc | Bio Rank | Cult Rank |  | Shutoff |  |  | Dst*Score
76 | 221 | NE | Santa Ysabel | 221-33R | 221-14 |  |  |  | 28.2432 | 2.5197 | 1 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 221 | 2.5197 | 71.1648
168 | 442 | EA | Glencliff | 442-2R | 442-16R | EOC |  |  | 15.3869 | 2.4598 | 2 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 442 | 2.4598 | 37.8495
98 | 237 | NE | Creelman | P117100 | EOC |  |  |  | 31.21 | 2.3197 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 2 | 3 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 237 | 2.3197 | 72.3975
82 | 222 | NE | Santa Ysabel | 222-8 | EOC |  |  |  | 38.3066 | 2.3196 | 4 | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 222 | 2.3196 | 88.8567
276 | 1030 | NE | Valley Center | 1030-14 | 1030-20R |  |  |  | 40.054 | 2.3196 | 5 | 3 | 2 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 2 | 1 | 1 | 3 |  |  | 1030 | 2.3196 | 92.9092
57 | 212 | NE | Warners | P19585 | EOC |  |  |  | 23.0977 | 2.3098 | 6 | 3 | 3 | 3 | 3 | 3 | 0 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 1 | 0 | 2 | 3 |  |  | 212 | 2.3098 | 53.3504
163 | 440 | EA | Glencliff | 440-6 | EOC |  |  |  | 12.2689 | 2.2899 | 7 | 3 | 2 | 3 | 3 | 3 | 0 | 2 | 2 | 2 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 440 | 2.2899 | 28.0944
206 | 520 | NE | Avocado | 520-33R | 520-1053 |  |  |  | 25.2805 | 2.2897 | 8 | 3 | 3 | 3 | 2 | 3 | 0 | 2 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 520 | 2.2897 | 57.8859
251 | 971 | NE | Creelman | 971 | 971-26R |  |  |  | 59.9191 | 2.2894 | 9 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 971 | 2.2894 | 137.1789
292 | 1233 | NE | Pala | 1233-252R | EOC |  |  |  | 22.833 | 2.2798 | 10 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 1233 | 2.2798 | 52.0539
277 | 1030 | NE | Valley Center | 1030-20R | EOC |  |  |  | 32.6343 | 2.2797 | 11 | 3 | 2 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 1 | 3 | 2 | 2 | 1 | 1 | 3 |  |  | 1030 | 2.2797 | 74.3955
253 | 971 | NE | Creelman | 971-24 | 971-306R | EOC |  |  | 21.5348 | 2.2698 | 12 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 971 | 2.2698 | 48.8795
95 | 236 | NE | Creelman | 236 | EOC |  |  |  | 45.9146 | 2.2695 | 13 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 236 | 2.2695 | 104.205
180 | 448 | EA | Cameron | 448-6 | 448-13R | 448-11R |  |  | 8.9731 | 2.2599 | 14 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 448 | 2.2599 | 20.2784
151 | 357 | EA | Alpine | 357 | 357-45R |  |  |  | 11.8898 | 2.2499 | 15 | 3 | 2 | 3 | 2 | 3 | 0 | 3 | 3 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 357 | 2.2499 | 26.7506
3 | 73 | EA | Descanso | 73 | 73-49R |  |  |  | 12.8051 | 2.2399 | 16 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 3 | 2 | 2 | 1 | 2 | 2 |  |  | 73 | 2.2399 | 28.6818
155 | 358 | EA | Alpine | 358-14 | EOC |  |  |  | 17.9513 | 2.2398 | 17 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 3 |  |  | 358 | 2.2398 | 40.2077
74 | 220 | NE | Santa Ysabel | P212213 | EOC |  |  |  | 33.3369 | 2.2297 | 18 | 3 | 3 | 2 | 3 | 3 | 0 | 2 | 1 | 3 | 2 | 2 | 3 | 2 | 2 | 0 | 1 | 2 |  |  | 220 | 2.2297 | 74.3302
81 | 222 | NE | Santa Ysabel | 222-1370R | EOC |  |  |  | 51 | 2.2295 | 19 | 3 | 3 | 2 | 2 | 3 | 1 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 222 | 2.2295 | 113.704
63 | 214 | NE | Rincon | 214-7 | 214-538 | EOC |  |  | 32.9292 | 2.2197 | 20 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 3 | 3 | 1 |  |  | 214 | 2.2197 | 73.0919
77 | 221 | NE | Santa Ysabel | 221-14 | P519130 | P478409 |  |  | 16.0578 | 2.2098 | 21 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 1 | 3 | 3 | 2 | 1 | 3 | 3 |  |  | 221 | 2.2098 | 35.4851
219 | 524 | EA | Jamacha | 524-13 | 524-34 |  |  |  | 38.5665 | 2.2096 | 22 | 3 | 1 | 3 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 524 | 2.2096 | 85.217
153 | 357 | EA | Alpine | 357-750R | EOC |  |  |  | 7.1138 | 2.1999 | 23 | 3 | 2 | 3 | 2 | 3 | 0 | 3 | 0 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 357 | 2.1999 | 15.6499
152 | 357 | EA | Alpine | 357-45R | 357-750R |  |  |  | 9.7472 | 2.1999 | 24 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 357 | 2.1999 | 21.4428
27 | 176 | NE | Poway | 176-26R | EOC |  |  |  | 36.4856 | 2.1996 | 25 | 3 | 1 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 2 |  |  | 176 | 2.1996 | 80.255
257 | 972 | NE | Creelman | P13262 | EOC |  |  |  | 15.6979 | 2.1898 | 26 | 3 | 2 | 2 | 3 | 3 | 1 | 2 | 0 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 1 |  |  | 972 | 2.1898 | 34.376
4 | 73 | EA | Descanso | 73-49R | 73-23R |  |  |  | 23.0691 | 2.1898 | 27 | 3 | 3 | 1 | 3 | 3 | 1 | 2 | 2 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 |  |  | 73 | 2.1898 | 50.5161
182 | 448 | EA | Cameron | 448-13R | 448-15R |  |  |  | 12.7725 | 2.1799 | 28 | 3 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 448 |  | 27.8425
103 | 240 | EA | Los Coches | 240 | 240-1097R | 240-1095R |  |  | 13.9318 | 2.1699 | 29 | 3 | 1 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 240 |  | 30.2301
183 | 448 | EA | Cameron | 448-15R | EOC |  |  |  | 14.9491 | 2.1699 | 30 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 448 |  | 32.4372
179 | 448 | EA | Cameron | 448 | 448-6 |  |  |  | 17.3138 | 2.1698 | 31 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 448 |  | 37.568
181 | 448 | EA | Cameron | 448-11R | EOC |  |  |  | 26.1881 | 2.1697 | 32 | 3 | 3 | 1 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 448 |  | 56.8212
70 | 217 | NE | Rincon | 217 | 217-835R |  |  |  | 45.561 | 2.1695 | 33 | 3 | 3 | 3 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 3 |  |  | 217 |  | 98.8466
162 | 440 | EA | Glencliff | 440 | 440-6 |  |  |  | 8.0581 | 2.1599 | 34 | 3 | 2 | 2 | 3 | 3 | 0 | 1 | 2 | 2 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 440 |  | 17.4049
169 | 442 | EA | Glencliff | 442-16R | EOC |  |  |  | 10.7032 | 2.1599 | 35 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 1 | 1 | 3 | 3 |  |  | 442 |  | 23.1178
154 | 358 | EA | Alpine | 358 | 358-14 |  |  |  | 11.2472 | 2.1599 | 36 | 3 | 2 | 2 | 2 | 3 | 0 | 3 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 358 |  | 24.2926
202 | 520 | NE | Avocado | 520-35R | 520-11 |  |  |  | 13.8597 | 2.1599 | 37 | 3 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 1 | 2 | 0 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 520 |  | 29.9349
220 | 524 | EA | Jamacha | 524-34 | EOC |  |  |  | 30.2254 | 2.1497 | 38 | 3 | 1 | 2 | 3 | 3 | 0 | 2 | 0 | 2 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 524 |  | 64.9754
21 | 157 | EA | Barrett | 157-75R | EOC |  |  |  | 34.9093 | 2.1397 | 39 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 157 |  | 74.6937
254 | 971 | NE | Creelman | 971-306R | EOC |  |  |  | 17.7968 | 2.1298 | 40 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 971 |  | 37.904
101 | 239 | NE | Pala | 239-15R | EOC |  |  |  | 18.8278 | 2.1298 | 41 | 3 | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 3 |  |  | 239 |  | 40.0998
201 | 520 | NE | Avocado | 520-26AE | 520-35R |  |  |  | 10.4591 | 2.1199 | 42 | 3 | 2 | 2 | 2 | 3 | 1 | 2 | 1 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 2 |  |  | 520 |  | 22.1722
140 | 351 | NE | Lilac | 351 | 351-819R |  |  |  | 10.6801 | 2.1199 | 43 | 3 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 351 |  | 22.6407
144 | 353 | NE | Lilac | 353-914R | EOC |  |  |  | 12.115 | 2.1199 | 44 | 3 | 2 | 3 | 2 | 3 | 1 | 3 | 2 | 1 | 2 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 353 |  | 25.6823
185 | 449 | EA | Cameron | 449-13R | EOC |  |  |  | 13.7621 | 2.1199 | 45 | 3 | 3 | 2 | 3 | 3 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 1 | 2 |  |  | 449 |  | 29.1738
290 | 1215 | EA | Crestwood | 1215 | EOC |  |  |  | 21.9858 | 2.1198 | 46 | 3 | 3 | 1 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 0 | 2 | 3 | 1 | 1 | 3 | 3 |  |  | 1215 |  | 46.6051
73 | 220 | NE | Santa Ysabel | 220-294R | P212213 |  |  |  | 11.5263 | 2.1099 | 47 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 2 | 2 | 0 | 3 | 3 |  |  | 220 |  | 24.3192
294 | 1250 | NE | Olivenhain | 1250 | 1250-9 |  |  |  | 15.9405 | 2.1098 | 48 | 1 | 2 | 3 | 3 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 1250 |  | 33.632
5 | 73 | EA | Descanso | 73-23R | EOC |  |  |  | 18.0922 | 2.1098 | 49 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 |  |  | 73 |  | 38.1713
278 | 1039 | NE | Ash | 1039-13AE | EOC |  |  |  | 13.2862 | 2.0999 | 50 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 2 | 3 | 1 | 1 | 1 |  |  | 1039 |  | 27.8992
23 | 157 | EA | Barrett | 157-87R | EOC |  |  |  | 33.3 | 2.0997 | 51 | 3 | 3 | 3 | 1 | 2 | 1 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 157 |  | 69.9189
240 | 907 | NE | Valley Center | 907 | 907-45 |  |  |  | 11.4294 | 2.0899 | 52 | 3 | 2 | 3 | 2 | 2 | 0 | 3 | 2 | 1 | 2 | 2 | 3 | 2 | 2 | 3 | 1 | 2 |  |  | 907 |  | 23.886
148 | 355 | EA | Alpine | 355 | EOC |  |  |  | 13.5146 | 2.0899 | 53 | 3 | 2 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 0 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 355 |  | 28.2437
241 | 907 | NE | Valley Center | 907-45 | EOC |  |  |  | 6.8528 | 2.0799 | 54 | 3 | 2 | 2 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 2 |  |  | 907 |  | 14.2534
149 | 356 | EA | Alpine | 356 | 356-19R |  |  |  | 12.1782 | 2.0799 | 55 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1 |  |  | 356 |  | 25.3292
80 | 222 | NE | Santa Ysabel | 222 | 222-1370R | 222-8 |  |  | 14.6 | 2.0799 | 56 | 3 | 3 | 2 | 1 | 3 | 0 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 2 | 0 | 1 | 1 |  |  | 222 |  | 30.3659
203 | 520 | NE | Avocado | 520-11 | 520-1054 | EOC |  |  | 15.9606 | 2.0798 | 57 | 3 | 2 | 3 | 2 | 3 | 0 | 1 | 1 | 1 | 2 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 520 |  | 33.1955
25 | 175 | NE | Poway | 175-90R | EOC |  |  |  | 20.7559 | 2.0798 | 58 | 3 | 2 | 2 | 2 | 2 | 1 | 3 | 2 | 1 | 3 | 0 | 3 | 3 | 3 | 1 | 1 | 1 |  |  | 175 |  | 43.1679
96 | 237 | NE | Creelman | 237 | 237-8 |  |  |  | 29.9326 | 2.0797 | 59 | 3 | 3 | 3 | 1 | 2 | 1 | 3 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 237 |  | 62.2508
167 | 442 | EA | Glencliff | 442 | 442-2R | EOC |  |  | 2.4383 | 2.07 | 60 | 3 | 3 | 1 | 3 | 3 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 3 | 2 |  |  | 442 |  | 5.0471
288 | 1166 | EA | Loveland | 1166-18R | 1166-1 | EOC |  |  | 8.3159 | 2.0699 | 61 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | 1166 |  | 17.2132
97 | 237 | NE | Creelman | 237-8 | P117100 | EOC |  |  | 14.7367 | 2.0699 | 62 | 3 | 3 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 0 | 3 | 3 | 2 | 1 | 3 | 1 |  |  | 237 |  | 30.5029
20 | 157 | EA | Barrett | 157-77R | EOC |  |  |  | 40.857 | 2.0696 | 63 | 3 | 3 | 2 | 1 | 2 | 0 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 157 |  | 84.5573
291 | 1233 | NE | Pala | 1233 | 1233-252R |  |  |  | 4.9167 | 2.06 | 64 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 2 | 1 |  |  | 1233 |  | 10.1281
66 | 214 | NE | Rincon | 214-16 | EOC |  |  |  | 6.7678 | 2.0599 | 65 | 3 | 3 | 2 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 3 | 2 | 3 |  |  | 214 |  | 13.9412
243 | 908 | NE | Valley Center | 908-23 | EOC |  |  |  | 30.1309 | 2.0597 | 66 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 908 |  | 62.0605
146 | 354 | NE | Lilac | 354-5 | 354-24AE | EOC |  |  | 36.9813 | 2.0596 | 67 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 3 | 1 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 354 |  | 76.1677
262 | 974 | NE | Creelman | 974-7 | EOC |  |  |  | 15.2072 | 2.0498 | 68 | 3 | 2 | 1 | 3 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 3 | 3 |  |  | 974 |  | 31.1724
305 | OK1 | NE | Oaks 1 | OK1 | EOC |  |  |  | 8.3875 | 2.0399 | 69 | 3 | 3 | 2 | 3 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | OK1 |  | 17.1098
289 | 1166 | EA | Loveland | 1166-1 | EOC |  |  |  | 10.6926 | 2.0399 | 70 | 3 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 2 |  |  | 1166 |  | 21.8118
160 | 411 | EA | Granite | 411-14R | 411-8 |  |  |  | 17.7886 | 2.0398 | 71 | 1 | 1 | 3 | 2 | 3 | 3 | 3 | 2 | 2 | 3 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 411 |  | 36.2857
55 | 211 | NE | Warners | 211-262R | EOC |  |  |  | 17.1311 | 2.0298 | 72 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 1 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 211 |  | 34.7731
232 | 599 | NE | San Marcos | P116474 | 599-1181 | EOC |  |  | 17.6703 | 2.0298 | 73 | 1 | 1 | 3 | 3 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 2 | 2 | 3 | 1 | 1 | 2 |  |  | 599 |  | 35.8675
186 | 449 | EA | Cameron | 449-1 | EOC |  |  |  | 5.9386 | 2.0199 | 74 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 0 | 3 | 3 |  |  | 449 |  | 11.9957
297 | CTL1 | NE | Crestline | CTL1 | EOC |  |  |  | 4.1521 | 2 | 75 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 0 | 2 | 0 | 1 | 2 |  |  | CTL1 |  | 8.304
306 | PE1 | NE | Pine Hills | PE1 | EOC |  |  |  | 6.8367 | 1.9999 | 76 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | PE1 |  | 13.673
142 | 352 | NE | Lilac | 352 | EOC |  |  |  | 11.4432 | 1.9999 | 77 | 3 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 0 | 1 | 2 |  |  | 352 |  | 22.8851
258 | 972 | NE | Creelman | 972-4 | EOC |  |  |  | 14.9597 | 1.9999 | 78 | 3 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 972 |  | 29.9171
295 | 1458 | EA | Alpine | 1458 | 1458-22 | EOC |  |  | 8.5532 | 1.9899 | 79 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 3 |  |  | 1458 |  | 17.0202
64 | 214 | NE | Rincon | 214-538 | 214-15 | 214-16 |  |  | 9.3754 | 1.9899 | 80 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 3 | 3 | 1 | 3 | 1 | 2 |  |  | 214 |  | 18.6561
184 | 449 | EA | Cameron | 449 | 449-1 | 449-13R |  |  | 11.3814 | 1.9899 | 81 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 1 | 2 |  |  | 449 |  | 22.6478
75 | 221 | NE | Santa Ysabel | 221 | 221-33R |  |  |  | 4.5674 | 1.98 | 82 | 3 | 3 | 1 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 221 |  | 9.0433
314 | SL1 | NE | Salton | SL1 | EOC |  |  |  | 4.8994 | 1.98 | 83 | 3 | 3 | 2 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 |  |  | SL1 |  | 9.7006
164 | 441 | EA | Glencliff | 441 | 441-27R | 441-30R |  |  | 10.8778 | 1.9799 | 84 | 3 | 2 | 1 | 3 | 3 | 1 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 441 |  | 21.5369
14 | 79 | EA | Descanso | 79-676R | 79-658R | EOC |  |  | 15.6057 | 1.9798 | 85 | 3 | 3 | 2 | 2 | 2 | 0 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 79 |  | 30.8968
100 | 239 | NE | Pala | 239 | 239-15R | EOC | EOC |  | 22.1875 | 1.9798 | 86 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 1 |  |  | 239 |  | 43.9263
71 | 217 | NE | Rincon | 217-835R | EOC |  |  |  | 26.3307 | 1.9797 | 87 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 217 |  | 52.1278
105 | 240 | EA | Los Coches | 240-1095R | EOC |  |  |  | 9.6335 | 1.9699 | 88 | 3 | 1 | 2 | 3 | 3 | 0 | 1 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 2 | 2 |  |  | 240 |  | 18.9771
273 | 1021 | NE | Lilac | 1021-48 | EOC |  |  |  | 12.9259 | 1.9699 | 89 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 1 | 2 |  |  | 1021 |  | 25.4624
193 | 470 | NE | Felicita | 470-18R | EOC |  |  |  | 23.211 | 1.9698 | 90 | 1 | 1 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 0 | 3 | 3 | 3 | 1 | 3 | 3 |  |  | 470 |  | 45.7203
296 | 1458 | EA | Alpine | 1458-22 | EOC |  |  |  | 9.3439 | 1.9599 | 91 | 3 | 2 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 1458 |  | 18.3132
141 | 351 | NE | Lilac | 351-819R | EOC |  |  |  | 10.5955 | 1.9599 | 92 | 1 | 2 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 1 | 2 | 1 |  |  | 351 |  | 20.766
68 | 215 | NE | Rincon | P216869 | EOC |  |  |  | 15.0229 | 1.9598 | 93 | 3 | 3 | 2 | 2 | 2 | 0 | 2 | 0 | 1 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 215 |  | 29.4427
138 | 350 | NE | Lilac | 350-46R | EOC |  |  |  | 20.2322 | 1.9598 | 94 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 350 |  | 39.651
54 | 211 | NE | Warners | 211-280R | EOC |  |  |  | 13.5968 | 1.9499 | 95 | 1 | 3 | 2 | 3 | 3 | 0 | 1 | 0 | 2 | 1 | 1 | 3 | 3 | 1 | 1 | 1 | 3 |  |  | 211 |  | 26.5119
285 | 1138 | EA | Santee | 1138-6R | EOC |  |  |  | 13.9085 | 1.9499 | 96 | 3 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 1138 |  | 27.1197
256 | 972 | NE | Creelman | 972-7 | P13262 |  |  |  | 15.3739 | 1.9498 | 97 | 3 | 2 | 3 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 972 |  | 29.9767
136 | 350 | NE | Lilac | 350-684R | EOC |  |  |  | 33.1557 | 1.9497 | 98 | 1 | 2 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 1 | 2 |  |  | 350 |  | 64.6426
316 | TM1 | NE | Temecula (SCE) | TM1 | EOC |  |  |  | 2.9864 | 1.94 | 99 | 3 | 2 | 1 | 3 | 3 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 0 | 1 | 2 |  |  | TM1 |  | 5.7935
252 | 971 | NE | Creelman | 971-26R | 971-24 |  |  |  | 9.2403 | 1.9399 | 100 | 3 | 2 | 2 | 3 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 971 |  | 17.9254
150 | 356 | EA | Alpine | 356-19R | EOC |  |  |  | 14.9436 | 1.9399 | 101 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 3 | 1 | 1 | 2 |  |  | 356 |  | 28.9883
242 | 908 | NE | Valley Center | 908 | 908-23 |  |  |  | 41.2864 | 1.9396 | 102 | 3 | 2 | 3 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 908 |  | 80.0785
52 | 210 | NE | Warners | P227546 | EOC |  |  |  | 10.2898 | 1.9299 | 103 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 2 | 2 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 210 |  | 19.8582
24 | 175 | NE | Poway | 175-24R | 175-90R |  |  |  | 14.2606 | 1.9299 | 104 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 3 | 3 |  |  | 175 |  | 27.5209
178 | 445 | EA | Boulevard | 445-24R | EOC |  |  |  | 22.6352 | 1.9298 | 105 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 0 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 445 |  | 43.6809
56 | 212 | NE | Warners | 212 | P19585 | 212-632R | 212-630R |  | 23.6792 | 1.9298 | 106 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 3 | 3 | 2 | 0 | 3 | 3 | 1 | 0 | 2 | 2 |  |  | 212 |  | 45.6952
72 | 220 | NE | Santa Ysabel | 220 | 220-294R |  |  |  | 7.4 | 1.9199 | 107 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 2 | 2 | 0 | 2 | 1 |  |  | 220 |  | 14.2075
10 | 78 | EA | Descanso | 78 | EOC |  |  |  | 12.1587 | 1.9099 | 108 | 3 | 3 | 1 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 3 | 3 |  |  | 78 |  | 23.2217
173 | 445 | EA | Boulevard | 445 | 445-23R | 445-17R | 445-19R | 445-21R | 11.1438 | 1.8999 | 109 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 3 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 445 |  | 21.1719
135 | 350 | NE | Lilac | 350 | 350-15R | 350-684R | 350-33R |  | 14.4254 | 1.8999 | 110 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 350 |  | 27.4061
272 | 1021 | NE | Lilac | 1021 | 1021-48 |  |  |  | 16.2631 | 1.8998 | 111 | 3 | 1 | 2 | 3 | 2 | 0 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 1 | 1 |  |  | 1021 |  | 30.8972
200 | 520 | NE | Avocado | 520 | 520-18R | 520-26AE |  |  | 18.6953 | 1.8998 | 112 | 1 | 2 | 2 | 2 | 3 | 0 | 3 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 520 |  | 35.5175
51 | 210 | NE | Warners | 210-9R | P227546 | EOC |  |  | 4.0625 | 1.89 | 113 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 3 |  |  | 210 |  | 7.678
205 | 520 | NE | Avocado | 520-18R | 520-33R |  |  |  | 7.3201 | 1.8899 | 114 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 520 |  | 13.8344
207 | 520 | NE | Avocado | 520-1053 | EOC |  |  |  | 17.4259 | 1.8898 | 115 | 1 | 2 | 2 | 2 | 3 | 0 | 1 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 2 | 1 | 2 |  |  | 520 |  | 32.932
174 | 445 | EA | Boulevard | 445-17R | EOC |  |  |  | 21.1485 | 1.8898 | 116 | 3 | 3 | 1 | 2 | 3 | 0 | 2 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 445 |  | 39.9662
61 | 212 | NE | Warners | 212-652R | EOC |  |  |  | 28.8727 | 1.8897 | 117 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 0 | 2 | 2 | 2 | 3 | 3 | 1 | 0 | 2 | 2 |  |  | 212 |  | 54.5611
177 | 445 | EA | Boulevard | 445-23R | 445-24R | EOC |  |  | 1.2598 | 1.88 | 118 | 3 | 3 | 1 | 2 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 445 |  | 2.3685
261 | 974 | NE | Creelman | 974 | 974-7 |  |  |  | 6.3195 | 1.8799 | 119 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 3 | 3 |  |  | 974 |  | 11.8803
175 | 445 | EA | Boulevard | 445-19R | EOC |  |  |  | 12.8462 | 1.8799 | 120 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 445 |  | 24.1492
139 | 350 | NE | Lilac | 350-33R | EOC |  |  |  | 15.0167 | 1.8798 | 121 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 350 |  | 28.2291
114 | 249 | NE | Pala | 249 | EOC |  |  |  | 15.0523 | 1.8798 | 122 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 0 | 3 | 2 | 2 | 0 | 3 | 3 |  |  | 249 |  | 28.296
287 | 1166 | EA | Loveland | 1166 | 1166-18R | EOC |  |  | 4.3964 | 1.87 | 123 | 3 | 2 | 1 | 3 | 3 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 2 | 1 |  |  | 1166 |  | 8.2211
15 | 79 | EA | Descanso | 79-658R | 79-660R |  |  |  | 13.2152 | 1.8699 | 124 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 79 |  | 24.7106
53 | 211 | NE | Warners | 211 | 211-280R | 211-262R |  |  | 15.0354 | 1.8698 | 125 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 2 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 2 |  |  | 211 |  | 28.114
303 | MAN1 | NE | Manzanita | MAN1 | EOC |  |  |  | 3.9542 | 1.86 | 126 | 3 | 3 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | MAN1 |  | 7.3546
274 | 1022 | NE | Lilac | 1022-15 | EOC |  |  |  | 7.8924 | 1.8599 | 127 | 3 | 1 | 2 | 3 | 2 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 0 | 3 | 2 | 1 | 1 |  |  | 1022 |  | 14.6793
259 | 973 | NE | Creelman | 973 | 973-27 | EOC |  |  | 12.5491 | 1.8599 | 128 | 3 | 2 | 1 | 1 | 3 | 1 | 2 | 3 | 0 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 |  |  | 973 |  | 23.3397
176 | 445 | EA | Boulevard | 445-21R | EOC |  |  |  | 25.8837 | 1.8597 | 129 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 445 |  | 48.137
170 | 444 | EA | Boulevard | 444 | P41993 |  |  |  | 6.5136 | 1.8499 | 130 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 1 | 1 | 1 | 3 |  |  | 444 |  | 12.0498
16 | 79 | EA | Descanso | 79-660R | 79-19R |  |  |  | 7.7002 | 1.8499 | 131 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 79 |  | 14.2448
104 | 240 | EA | Los Coches | 240-1097R | EOC |  |  |  | 12.7585 | 1.8499 | 132 | 3 | 1 | 1 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 240 |  | 23.6016
60 | 212 | NE | Warners | 212-650R | EOC |  |  |  | 21.3939 | 1.8498 | 133 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 2 | 2 | 3 | 3 | 3 | 1 | 0 | 2 | 1 |  |  | 212 |  | 39.5742
172 | 444 | EA | Boulevard | P42077 | EOC |  |  |  | 23.6938 | 1.8498 | 134 | 1 | 3 | 1 | 2 | 3 | 2 | 2 | 1 | 3 | 2 | 0 | 2 | 3 | 1 | 1 | 2 | 3 |  |  | 444 |  | 43.8278
22 | 157 | EA | Barrett | 157-67R | 157-87R | 157-75R | 157-77R |  | 2.1 | 1.84 | 135 | 3 | 3 | 0 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 1 | 3 | 1 |  |  | 157 |  | 3.864
275 | 1030 | NE | Valley Center | 1030 | 1030-14 |  |  |  | 4.7856 | 1.84 | 136 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 3 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 1030 |  | 8.8053
166 | 441 | EA | Glencliff | 441-30R | EOC |  |  |  | 6.1053 | 1.8399 | 137 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 441 |  | 11.2334
211 | 521 | NE | Avocado | 521-32R | EOC |  |  |  | 9.1759 | 1.8399 | 138 | 3 | 2 | 2 | 1 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 521 |  | 16.8829
58 | 212 | NE | Warners | 212-632R | 212-650R | 212-652R |  |  | 11.8131 | 1.8399 | 139 | 1 | 3 | 1 | 3 | 3 | 1 | 1 | 0 | 2 | 2 | 1 | 3 | 3 | 1 | 0 | 1 | 2 |  |  | 212 |  | 21.7346
145 | 354 | NE | Lilac | 354 | 354-5 |  |  |  | 17.6538 | 1.8398 | 140 | 1 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 354 |  | 32.4799
171 | 444 | EA | Boulevard | P41993 | P42077 |  |  |  | 7.8121 | 1.8299 | 141 | 3 | 3 | 1 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 1 | 1 | 1 | 3 |  |  | 444 |  | 14.2956
1 | 67 | EA | Barrett | 67 | 67-24R |  |  |  | 35.8356 | 1.8296 | 142 | 3 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 2 |  |  | 67 |  | 65.5663
65 | 214 | NE | Rincon | 214-15 | EOC |  |  |  | 3.8729 | 1.82 | 143 | 3 | 2 | 1 | 2 | 3 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 3 | 3 | 2 |  |  | 214 |  | 7.0486
50 | 210 | NE | Warners | 210 | 210-9R |  |  |  | 6.1955 | 1.8199 | 144 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 1 |  |  | 210 |  | 11.2753
165 | 441 | EA | Glencliff | 441-27R | EOC |  |  |  | 6.7186 | 1.8199 | 145 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 441 |  | 12.2273
231 | 597 | NE | San Marcos | 597-636 | EOC |  |  |  | 12.7426 | 1.8199 | 146 | 1 | 1 | 3 | 2 | 2 | 0 | 3 | 1 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 2 | 2 |  |  | 597 |  | 23.1899
87 | 230 | NE | Monserate | 230-133 | EOC |  |  |  | 17.6042 | 1.8198 | 147 | 3 | 1 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 230 |  | 32.0365
311 | RB1 | NE | Rainbow 1 | RB1-19R | EOC |  |  |  | 5.9968 | 1.8099 | 148 | 3 | 2 | 1 | 3 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 0 | 2 | 2 | 1 | 1 |  |  | RB1 |  | 10.8538
69 | 216 | NE | Rincon | 216 | EOC |  |  |  | 6.6792 | 1.8099 | 149 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 0 | 3 | 3 |  |  | 216 |  | 12.0888
59 | 212 | NE | Warners | 212-630R | EOC |  |  |  | 3.6169 | 1.8 | 150 | 1 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 3 | 1 | 0 | 3 | 1 |  |  | 212 |  | 6.5102
213 | 521 | NE | Avocado | 521-14R | EOC |  |  |  | 11.8812 | 1.7999 | 151 | 3 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 2 | 2 | 1 | 2 | 3 | 2 | 1 | 2 | 2 |  |  | 521 |  | 21.3848
91 | 233 | NE | Monserate | 233-49 | EOC |  |  |  | 24.2447 | 1.7998 | 152 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 3 | 2 | 3 | 1 | 2 | 3 | 2 | 1 | 2 | 3 |  |  | 233 |  | 43.6346
302 | JU1 | NE | Julian | JU1 | EOC |  |  |  | 2.5316 | 1.79 | 153 | 3 | 3 | 1 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 |  |  | JU1 |  | 4.5316
204 | 520 | NE | Avocado | 520-1054 | 520-13 |  |  |  | 5.1127 | 1.7899 | 154 | 3 | 2 | 1 | 2 | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 3 | 2 | 2 | 1 | 1 |  |  | 520 |  | 9.1515
67 | 215 | NE | Rincon | 215 | P216869 |  |  |  | 8.8807 | 1.7899 | 155 | 3 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 215 |  | 15.8956
92 | 233 | NE | Monserate | 233-14 | EOC |  |  |  | 22.4464 | 1.7898 | 156 | 1 | 1 | 3 | 1 | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 2 | 3 |  |  | 233 |  | 40.174
137 | 350 | NE | Lilac | 350-15R | 350-46R |  |  |  | 29.4682 | 1.7897 | 157 | 1 | 2 | 2 | 2 | 2 | 0 | 3 | 1 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 1 | 1 |  |  | 350 |  | 52.7394
93 | 234 | NE | Monserate | 234 | EOC |  |  |  | 17.8201 | 1.7798 | 158 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 234 |  | 31.7166
161 | 411 | EA | Granite | 411-8 | EOC |  |  |  | 7.1159 | 1.7699 | 159 | 1 | 1 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 411 |  | 12.5947
208 | 521 | NE | Avocado | 521 | 521-27R | 521-18R |  |  | 14.1765 | 1.7699 | 160 | 3 | 2 | 3 | 1 | 1 | 0 | 3 | 3 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 521 |  | 25.0904
84 | 230 | NE | Monserate | 230-4R | 230-11 | EOC |  |  | 24.6432 | 1.7698 | 161 | 3 | 1 | 3 | 1 | 2 | 2 | 3 | 1 | 2 | 3 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 230 |  | 43.6124
11 | 79 | EA | Descanso | 79 | 79-676R | 79-673R |  |  | 6.5 | 1.7599 | 162 | 3 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 79 |  | 11.4396
17 | 79 | EA | Descanso | 79-19R | EOC |  |  |  | 9.0712 | 1.7599 | 163 | 3 | 3 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 3 | 3 | 1 | 1 | 1 | 1 |  |  | 79 |  | 15.9645
102 | 239 | NE | Pala | EOC | EOC |  |  |  | 11.9314 | 1.7599 | 164 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 2 | 1 |  |  | 239 |  | 20.9979
8 | 75 | EA | Jamacha | 75-32R | P171361 |  |  |  | 16.2623 | 1.7598 | 165 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 1 | 2 | 2 | 0 | 3 | 3 | 2 | 3 | 1 | 2 |  |  | 75 |  | 28.619
88 | 231 | NE | Monserate | 231 | Z317920 |  |  |  | 32.7089 | 1.7397 | 166 | 1 | 1 | 3 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 231 |  | 56.9028
147 | 354 | NE | Lilac | 354-24AE | EOC |  |  |  | 3.5104 | 1.71 | 167 | 1 | 2 | 1 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 2 | 1 | 2 | 2 |  |  | 354 |  | 6.0027
310 | RB1 | NE | Rainbow 1 | RB1 | RB1-19R |  |  |  | 9.328 | 1.7099 | 168 | 3 | 2 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 1 | 1 |  |  | RB1 |  | 15.9501
260 | 973 | NE | Creelman | 973-626R | EOC |  |  |  | 10.7032 | 1.6999 | 169 | 3 | 2 | 1 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 3 | 2 | 2 | 1 | 1 | 1 |  |  | 973 |  | 18.1943
117 | 283 | EA | Loveland | 283 | 283-29 |  |  |  | 5.4028 | 1.6899 | 170 | 3 | 2 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 283 |  | 9.1305
209 | 521 | NE | Avocado | 521-18R | 521-5 |  |  |  | 11.3989 | 1.6899 | 171 | 3 | 3 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 521 |  | 19.2628
158 | 396 | EA | Santee | P970961 | EOC |  |  |  | 12.3117 | 1.6899 | 172 | 1 | 1 | 3 | 2 | 3 | 0 | 2 | 1 | 2 | 2 | 0 | 1 | 3 | 2 | 0 | 1 | 1 |  |  | 396 |  | 20.8053
13 | 79 | EA | Descanso | Z371551 | P377371 | EOC |  |  | 2.1905 | 1.68 | 173 | 3 | 3 | 0 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 79 |  | 3.68
298 | DV1 | EA | Dehesa Valley | DV1 | EOC |  |  |  | 5.9562 | 1.6799 | 174 | 3 | 2 | 2 | 2 | 2 | 0 | 2 | 0 | 1 | 2 | 0 | 2 | 0 | 2 | 1 | 2 | 1 |  |  | DV1 |  | 10.0061
212 | 521 | NE | Avocado | 521-27R | 521-14R |  |  |  | 19.5106 | 1.6798 | 175 | 1 | 3 | 2 | 1 | 1 | 1 | 3 | 2 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 521 |  | 32.774
113 | 248 | EA | Los Coches | 248 | EOC |  |  |  | 21.5934 | 1.6798 | 176 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 248 |  | 36.2722
271 | 1001 | NC | Rancho Santa Fe | 1001-39 | EOC |  |  |  | 4.7752 | 1.67 | 177 | 1 | 1 | 3 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 1 |  |  | 1001 |  | 7.9743
19 | 91 | EA | Jamacha | P370004 | EOC |  |  |  | 5.7009 | 1.6699 | 178 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | 1 |  |  | 91 |  | 9.5203
245 | 909 | NE | Valley Center | 909-6 | EOC |  |  |  | 11.1458 | 1.6699 | 179 | 3 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 2 | 2 | 0 | 3 | 3 |  |  | 909 |  | 18.6123
233 | 599 | NE | San Marcos | 599-1181 | EOC |  |  |  | 6.2038 | 1.6599 | 180 | 1 | 1 | 1 | 3 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 2 | 2 | 3 | 1 | 1 | 2 |  |  | 599 |  | 10.2979
143 | 353 | NE | Lilac | 353 | 353-914R |  |  |  | 6.7023 | 1.6599 | 181 | 1 | 2 | 1 | 2 | 3 | 0 | 2 | 2 | 0 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 353 |  | 11.1253
2 | 67 | EA | Barrett | 67-24R | EOC |  |  |  | 12.1398 | 1.6599 | 182 | 3 | 2 | 2 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 67 |  | 20.1505
6 | 75 | EA | Jamacha | 75-996R | 75-40 |  |  |  | 14.7434 | 1.6599 | 183 | 1 | 1 | 2 | 1 | 2 | 1 | 3 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 3 | 2 | 2 |  |  | 75 |  | 24.4718
90 | 233 | NE | Monserate | 233 | 233-49 | 233-14 |  |  | 16.7288 | 1.6598 | 184 | 1 | 1 | 3 | 1 | 2 | 0 | 3 | 3 | 2 | 3 | 0 | 2 | 3 | 2 | 1 | 1 | 2 |  |  | 233 |  | 27.767
157 | 387 | EA | Granite | Z272783 | EOC |  |  |  | 3.4345 | 1.65 | 185 | 1 | 2 | 0 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 1 | 2 | 2 |  |  | 387 |  | 5.6668
78 | 221 | NE | Santa Ysabel | P519130 | EOC |  |  |  | 14.7973 | 1.6499 | 186 | 3 | 3 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 3 | 3 | 2 | 1 | 1 | 3 |  |  | 221 |  | 24.4134
125 | 307 | NC | Rancho Santa Fe | EOC | EOC |  |  |  | 3.7222 | 1.64 | 187 | 1 | 2 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 3 | 2 |  |  | 307 |  | 6.1042
247 | 920 | NE | Pomerado | P108024 | EOC |  |  |  | 4.9241 | 1.64 | 188 | 1 | 1 | 1 | 3 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 2 |  |  | 920 |  | 8.0752
307 | RA1 | NE | Ramona | RA1 | EOC |  |  |  | 10.767 | 1.6399 | 189 | 3 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | RA1 |  | 17.6568
215 | 522 | NE | Avocado | 522-25 | EOC |  |  |  | 14.515 | 1.6399 | 190 | 1 | 2 | 3 | 1 | 1 | 1 | 3 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 522 |  | 23.8024
12 | 79 | EA | Descanso | 79-673R | Z371551 |  |  |  | 10.3 | 1.6199 | 191 | 3 | 3 | 0 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 3 | 1 | 1 | 1 | 2 |  |  | 79 |  | 16.6849
26 | 176 | NE | Poway | 176 | 176-26R | 176-36R |  |  | 14.0405 | 1.6099 | 192 | 1 | 1 | 2 | 2 | 2 | 0 | 3 | 2 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 176 |  | 22.6033
244 | 909 | NE | Valley Center | 909 | 909-6 |  |  |  | 17.4189 | 1.6098 | 193 | 3 | 2 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 3 | 0 | 2 | 2 | 2 | 0 | 1 | 2 |  |  | 909 |  | 28.0415
9 | 75 | EA | Jamacha | P171361 | EOC |  |  |  | 15.3894 | 1.5898 | 194 | 3 | 1 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 1 | 0 | 3 | 3 | 1 | 3 | 3 | 3 |  |  | 75 |  | 24.4668
246 | 920 | NE | Pomerado | P137565 | EOC |  |  |  | 1.989 | 1.57 | 195 | 1 | 1 | 0 | 3 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 3 | 1 |  |  | 920 |  | 3.1227
304 | MOR1 | NE | Moore | MOR1 | EOC |  |  |  | 2.8384 | 1.57 | 196 | 3 | 2 | 2 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | MOR1 |  | 4.4563
210 | 521 | NE | Avocado | 521-5 | 521-32R |  |  |  | 10.7176 | 1.5699 | 197 | 3 | 2 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 2 | 0 | 3 | 3 | 2 | 1 | 2 | 1 |  |  | 521 |  | 16.8255
110 | 246 | EA | Los Coches | 246-9 | 246-11 |  |  |  | 11.429 | 1.5699 | 198 | 1 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 1 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 3 |  |  | 246 |  | 17.9422
218 | 524 | EA | Jamacha | 524-30 | 524-13 |  |  |  | 3.272 | 1.56 | 199 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 524 |  | 5.1042
194 | 470 | NE | Felicita | 470-30 | EOC |  |  |  | 5.5282 | 1.5599 | 200 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 3 | 1 | 1 | 1 |  |  | 470 |  | 8.6237
187 | 450 | NE | Ash | 450-18 | EOC |  |  |  | 8.5977 | 1.5599 | 201 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 3 | 1 | 1 | 1 | 2 |  |  | 450 |  | 13.4117
28 | 176 | NE | Poway | 176-36R | EOC |  |  |  | 8.5275 | 1.5499 | 202 | 3 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 176 |  | 13.2168
94 | 235 | NE | Creelman | 235 | EOC |  |  |  | 14.8273 | 1.5499 | 203 | 1 | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 2 | 2 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 235 |  | 22.9801
159 | 411 | EA | Granite | P172406 | 411-14R |  |  |  | 1.8231 | 1.53 | 204 | 1 | 1 | 0 | 2 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 1 | 2 | 2 |  |  | 411 |  | 2.7893
255 | 972 | NE | Creelman | 972 | 972-7 | 972-4 |  |  | 7.2384 | 1.5299 | 205 | 1 | 2 | 2 | 1 | 1 | 1 | 3 | 3 | 1 | 2 | 0 | 1 | 3 | 2 | 2 | 1 | 1 |  |  | 972 |  | 11.0743
230 | 597 | NE | San Marcos | 597-35 | 597-636 |  |  |  | 4.582 | 1.52 | 206 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 3 | 1 | 2 | 1 |  |  | 597 |  | 6.9644
118 | 283 | EA | Loveland | 283-29 | 283-26 |  |  |  | 8.5809 | 1.5199 | 207 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 2 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 1 | 2 |  |  | 283 |  | 13.0422
45 | 204 | OC | San Mateo | 204-6 | EOC |  |  |  | 8.9962 | 1.5199 | 208 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 204 |  | 13.6734
7 | 75 | EA | Jamacha | 75-40 | 75-32R |  |  |  | 10.9716 | 1.5199 | 209 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 1 | 2 | 3 | 2 | 3 | 1 | 1 |  |  | 75 |  | 16.6756
44 | 204 | OC | San Mateo | 204-2 | 204-6 |  |  |  | 12.6553 | 1.5199 | 210 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 204 |  | 19.2345
119 | 283 | EA | Loveland | 283-26 | EOC |  |  |  | 4.7106 | 1.51 | 211 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 283 |  | 7.1128
315 | SSC1 | OC | So San Clemente | SSC1 | SSC1-3 |  |  |  | 1.1203 | 1.5 | 212 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 |  |  | SSC1 |  | 1.6804
62 | 214 | NE | Rincon | 214 | 214-10 | 214-7 |  |  | 8.1002 | 1.4899 | 213 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 2 | 1 | 2 | 0 | 2 | 3 | 2 | 3 | 1 | 1 |  |  | 214 |  | 12.0686
129 | 327 | NE | Warren Canyon | 327 | EOC |  |  |  | 0.88636 | 1.48 | 214 | 1 | 2 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 | 3 | 1 |  |  | 327 |  | 1.3118
286 | 1138 | EA | Santee | 1138-22 | EOC |  |  |  | 2.4225 | 1.48 | 215 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 1138 |  | 3.5853
293 | 1235 | NE | Monserate | 1235 | EOC |  |  |  | 16.8837 | 1.4798 | 216 | 1 | 2 | 3 | 1 | 1 | 0 | 3 | 2 | 2 | 3 | 0 | 2 | 0 | 2 | 1 | 1 | 1 |  |  | 1235 |  | 24.985
189 | 454 | NE | Ash | 454-15 | EOC |  |  |  | 3.7525 | 1.47 | 217 | 1 | 1 | 1 | 3 | 3 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 1 | 1 |  |  | 454 |  | 5.516
79 | 221 | NE | Santa Ysabel | P478409 | EOC |  |  |  | 23.4551 | 1.4698 | 218 | 1 | 3 | 0 | 1 | 2 | 0 | 1 | 0 | 2 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 3 |  |  | 221 |  | 34.4735
214 | 522 | NE | Avocado | 522 | 522-25 |  |  |  | 5.5396 | 1.4599 | 219 | 1 | 2 | 2 | 1 | 1 | 0 | 2 | 3 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 522 |  | 8.0875
198 | 502 | NE | Chicarita | 502-28 | EOC |  |  |  | 1.3011 | 1.45 | 220 | 1 | 1 | 1 | 3 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 | 2 | 2 |  |  | 502 |  | 1.8866
42 | 204 | OC | San Mateo | 204 | 204-24 | 204-2 | EOC |  | 6.3936 | 1.4499 | 221 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 204 |  | 9.2703
85 | 230 | NE | Monserate | 230-4R | 230-133 |  |  |  | 7.039 | 1.4499 | 222 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 1 | 2 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 230 |  | 10.2061
127 | 315 | OC | Capistrano | 315-2 | 315-502 |  |  |  | 5.84 | 1.4399 | 223 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 1 |  |  | 315 |  | 8.4092
18 | 91 | EA | Jamacha | Z971734 | 91-649 |  |  |  | 0.84886 | 1.43 | 224 | 1 | 3 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 |  |  | 91 |  | 1.2139
263 | 975 | NE | Creelman | 975 | 975-2 |  |  |  | 4.1525 | 1.43 | 225 | 1 | 2 | 1 | 1 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 2 | 2 |  |  | 975 |  | 5.9378
33 | 185 | NE | Escondido | P417773 | EOC |  |  |  | 5.4458 | 1.4199 | 226 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 185 |  | 7.7328
312 | RC1 | NE | Reidy Canyon | RC1 | EOC |  |  |  | 2.6373 | 1.41 | 227 | 1 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 2 |  |  | RC1 |  | 3.7185
111 | 246 | EA | Los Coches | 246-11 | EOC |  |  |  | 9.2875 | 1.3999 | 228 | 1 | 1 | 2 | 1 | 1 | 0 | 3 | 1 | 2 | 2 | 0 | 2 | 3 | 2 | 2 | 1 | 1 |  |  | 246 |  | 13.0016
86 | 230 | NE | Monserate | 230-11 | EOC |  |  |  | 10.4443 | 1.3999 | 229 | 1 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 1 | 2 | 0 | 1 | 3 | 3 | 1 | 1 | 1 |  |  | 230 |  | 14.621
190 | 455 | NE | Ash | 455-979 | 455-34 | EOC |  |  | 4.0966 | 1.39 | 230 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | 455 |  | 5.6941
299 | FB1 | NE | Fallbrook 1 | FB1 | EOC |  |  |  | 4.1939 | 1.39 | 231 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 0 | 2 | 1 | 2 | 1 | 1 | 1 |  |  | FB1 |  | 5.8294
134 | 339 | OC | Cristianitos | 339 | EOC |  |  |  | 9.4475 | 1.3899 | 232 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 2 | 2 |  |  | 339 |  | 13.1312
121 | 300 | NC | Pendleton | 300-1 | 300-25 | EOC |  |  | 11.622 | 1.3899 | 233 | 1 | 2 | 1 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 300 |  | 16.1532
116 | 260 | CM | Otay Lakes | 260 | EOC |  |  |  | 12.5536 | 1.3899 | 234 | 1 | 1 | 1 | 2 | 1 | 0 | 2 | 3 | 2 | 1 | 0 | 3 | 0 | 2 | 1 | 3 | 3 |  |  | 260 |  | 17.4479
40 | 202 | NC | Las Pulgas | 202 | EOC |  |  |  | 12.603 | 1.3899 | 235 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 202 |  | 17.5166
309 | RA3 | NE | Ramona | RA3 | EOC |  |  |  | 3.068 | 1.38 | 236 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 3 | 2 | 0 | 1 | 1 |  |  | RA3 |  | 4.2337
188 | 452 | NE | Ash | 452-748 | EOC |  |  |  | 4.5273 | 1.38 | 237 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 2 | 1 |  |  | 452 |  | 6.2474
130 | 329 | OC | San Mateo | 329 | EOC |  |  |  | 4.5527 | 1.38 | 238 | 1 | 2 | 0 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 2 | 1 |  |  | 329 |  | 6.2825
30 | 182 | NE | Escondido | 182-354 | P510606 | Z16125 | EOC |  | 10.4362 | 1.3799 | 239 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 2 | 1 | 1 | 3 | 2 | 1 | 1 | 3 |  |  | 182 |  | 14.4008
300 | FB2 | NE | Fallbrook 2 | FB2 | EOC |  |  |  | 3.8405 | 1.37 | 240 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | FB2 |  | 5.2614
234 | 728 | BC | Scripps | 728-689 | EOC |  |  |  | 2.086 | 1.36 | 241 | 1 | 1 | 0 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 0 | 3 | 1 | 3 | 1 |  |  | 728 |  | 2.8369
122 | 300 | NC | Pendleton | 300-25 | EOC |  |  |  | 5.5492 | 1.3599 | 242 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 3 | 3 |  |  | 300 |  | 7.5467
216 | 523 | NE | Avocado | 523 | 523-31AE |  |  |  | 3.7097 | 1.35 | 243 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 523 |  | 5.0079
270 | 1001 | NC | Rancho Santa Fe | P132166 | EOC |  |  |  | 2.1189 | 1.32 | 244 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 1 |  |  | 1001 |  | 2.797
38 | 200 | OC | San Mateo | 200 | 200-29 | EOC |  |  | 3.1027 | 1.32 | 245 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 2 | 3 | 1 |  |  | 200 |  | 4.0954
123 | 307 | NC | Rancho Santa Fe | P230241 | EOC |  |  |  | 0.7428 | 1.31 | 246 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 1 | 1 |  |  | 307 |  | 0.97307
308 | RA2 | NE | Ramona | RA2 | EOC |  |  |  | 2.8767 | 1.31 | 247 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 1 |  |  | RA2 |  | 3.7684
43 | 204 | OC | San Mateo | 204-24 | EOC |  |  |  | 5.0672 | 1.3099 | 248 | 1 | 1 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 2 | 1 | 3 | 3 |  |  | 204 |  | 6.6378
191 | 455 | NE | Ash | 455-926 | 455-34 | EOC |  |  | 1.7877 | 1.3 | 249 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 0 | 1 | 1 |  |  | 455 |  | 2.324
217 | 523 | NE | Avocado | 523-31AE | EOC |  |  |  | 2.7553 | 1.3 | 250 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  |  | 523 |  | 3.5818
124 | 307 | NC | Rancho Santa Fe | Z12392 | EOC |  |  |  | 5.7 | 1.2899 | 251 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 1 | 2 | 2 |  |  | 307 |  | 7.3527
283 | 1101 | NE | Artesian | 1101-1 | P819071 |  |  |  | 3.0506 | 1.28 | 252 | 1 | 2 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 3 | 1 |  |  | 1101 |  | 3.9046
49 | 209 | NC | Melrose | P214248 | EOC |  |  |  | 2.4578 | 1.25 | 253 | 1 | 1 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 2 | 1 | 1 |  |  | 209 |  | 3.0721
132 | 331 | OC | San Mateo | 331-2 | EOC |  |  |  | 2.8953 | 1.25 | 254 | 1 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 1 |  |  | 331 |  | 3.619
112 | 247 | EA | Los Coches | 247-14 | P33699 |  |  |  | 5.5227 | 1.2399 | 255 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 3 | 2 | 2 | 1 | 1 |  |  | 247 |  | 6.8479
34 | 188 | NE | Escondido | P216702 | EOC |  |  |  | 0.9428 | 1.23 | 256 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 1 | 1 |  |  | 188 |  | 1.1596
222 | 536 | CM | Border | Z135595 | EOC |  |  |  | 3.3883 | 1.23 | 257 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 1 | 1 | 1 | 2 | 3 |  |  | 536 |  | 4.1674
89 | 232 | NE | Monserate | 232 | EOC |  |  |  | 4.967 | 1.21 | 258 | 1 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 232 |  | 6.0099
221 | 527 | OC | Las Pulgas | 527 | EOC |  |  |  | 6.2663 | 1.1899 | 259 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3 | 3 |  |  | 527 |  | 7.4565
37 | 198 | NC | San Luis Rey | 198-4 | P121327 | Z29143 |  |  | 0.48769 | 1.18 | 260 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 3 | 3 |  |  | 198 |  | 0.57547
133 | 338 | OC | Cristianitos | 338 | EOC |  |  |  | 0.91439 | 1.18 | 261 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 1 |  |  | 338 |  | 1.079
224 | 542 | NE | Bernardo | 542 | 542-13 |  |  |  | 1.8415 | 1.18 | 262 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 2 | 2 |  |  | 542 |  | 2.1729
237 | 791 | NE | Felicita | 791-26 | EOC |  |  |  | 4.943 | 1.18 | 263 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 0 | 3 | 0 | 2 | 1 |  |  | 791 |  | 5.8325
282 | 1100 | NE | Artesian | P515154 | EOC |  |  |  | 1.2008 | 1.17 | 264 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 |  |  | 1100 |  | 1.4049
36 | 197 | OC | Capistrano | 197-19 | EOC |  |  |  | 1.4297 | 1.17 | 265 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 3 | 2 |  |  | 197 |  | 1.6728
281 | 1100 | NE | Artesian | 1100 | 1100-46 | EOC |  |  | 2.458 | 1.17 | 266 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 | 0 | 3 | 1 |  |  | 1100 |  | 2.8757
31 | 182 | NE | Escondido | P510606 | P810041 | P113377 | EOC |  | 6.4737 | 1.1699 | 267 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 3 | 2 | 1 | 1 | 1 |  |  | 182 |  | 7.5738
39 | 200 | OC | San Mateo | 200-28 | 200-6 | 200-438 |  |  | 0.4553 | 1.12 | 268 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 3 | 2 | 1 | 1 |  |  | 200 |  | 0.50994
48 | 206 | NC | Melrose | 206-1105 | EOC |  |  |  | 4.8136 | 1.12 | 269 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 3 | 2 | 1 | 1 | 1 |  |  | 206 |  | 5.391
128 | 315 | OC | Capistrano | 315-501 | EOC |  |  |  | 0.47576 | 1.11 | 270 | 1 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 2 |  |  | 315 |  | 0.52809
223 | 540 | NE | Bernardo | 540 | 540-2 |  |  |  | 0.95871 | 1.11 | 271 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 2 | 1 |  |  | 540 |  | 1.0642
106 | 242 | EA | Los Coches | 242 | 241-T6-242 |  |  |  | 2.3888 | 1.11 | 272 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 1 |  |  | 242 |  | 2.6515
249 | 970 | NE | Creelman | 970 | 970-10 |  |  |  | 2.2697 | 1.09 | 273 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 2 | 0 | 3 | 2 |  |  | 970 |  | 2.4739
32 | 185 | NE | Escondido | P114604 | EOC |  |  |  | 0.88409 | 1.08 | 274 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 1 | 1 |  |  | 185 |  | 0.95481
107 | 242 | EA | Los Coches | P970731 | EOC |  |  |  | 1.7996 | 1.08 | 275 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 1 | 1 |  |  | 242 |  | 1.9436
115 | 252 | BC | Kearny | P36981 | EOC |  |  |  | 4.1129 | 1.08 | 276 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 1 | 3 | 3 | 3 |  |  | 252 |  | 4.4417
236 | 776 | BC | Mesa Heights | 776-8 | EOC |  |  |  | 2.1811 | 1.07 | 277 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 3 | 1 |  |  | 776 |  | 2.3337
229 | 594 | CM | Proctor Valley | P166873 | EOC |  |  |  | 1.8324 | 1.06 | 278 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 3 | 0 | 2 | 0 | 3 | 1 |  |  | 594 |  | 1.9423
41 | 203 | OC | San Mateo | 203 | 203-7 |  |  |  | 2.5756 | 1.06 | 279 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 3 | 1 | 1 | 1 |  |  | 203 |  | 2.73
47 | 205 | NC | Melrose | P116036 | EOC |  |  |  | 0.4911 | 1.04 | 280 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 1 |  |  | 205 |  | 0.51074
313 | SE4 | OC | Serra | SE4 | EOC |  |  |  | 0.59299 | 1.03 | 281 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 1 |  |  | SE4 |  | 0.61078
248 | 968 | BC | Eastgate | 968-14 | EOC |  |  |  | 2.1536 | 1.03 | 282 | 1 | 1 | 0 | 2 | 2 | 1 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 3 | 1 |  |  | 968 |  | 2.2182
46 | 205 | NC | Melrose | P111778 | EOC |  |  |  | 0.70625 | 0.95999 | 283 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 1 |  |  | 205 |  | 0.678
235 | 770 | BC | Mesa Heights | Z90080 | EOC |  |  |  | 1.8898 | 0.93998 | 284 | 1 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3 | 1 |  |  | 770 |  | 1.7764
192 | 463 | CM | San Ysidro | P108483 | EOC |  |  |  | 1.9051 | 0.92998 | 285 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 1 |  |  | 463 |  | 1.7717
131 | 330 | OC | San Mateo | 330-10 | P25224 |  |  |  | 1.4953 | 0.67999 | 286 | 1 | 2 | 1 | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  |  | 330 |  | 1.0168
| A | Circuit
| B | Study segment boundaries
| C | Length in miles of the study segment
| D | Weighted score
| E | Ranking
| 1 | Risk zone: HRFA: 3, FTZ: 1 | [9 empty] | 8%
| 2 | Wind Factor: Based on the forecasted frequency of extreme wind events - (Brian D'Agostino) | [9 empty] | 12%
| 3 | Tree Factor: Density of trees in proximity >=40ft weighted by species (Vegetation Management) | [9 empty] | 10%
| 4 | Fuel: (Fire Coordinator) | [9 empty] | 12%
| 5 | Fire ignition risk: (Fire Coordinator) | [9 empty] | 10% | 52%
| 6 | Capacitor factor - number of capacitors in segment (TDAM) | [9 empty] | 3%
| 7 | Expulsion fuse factor (TDAM) | [9 empty] | 3%
| 8 | Switch factor (TDAM) | [9 empty] | 2%
| 9 | Conductor factor -smaller than 2/0- (TDAM) | [9 empty] | 2%
| 10 | Transformer factor (TDAM) | [9 empty] | 2%
| 11 | High-risk transformer factor (TDAM) | [9 empty] | 2%
| 12 | Ranking by district operating center | [9 empty] | 4%
| 13 | 5-Year Outage History Index (TDAM) | [9 empty] | 5% | 23%
| 14 | Relative structure value in projected burn path (Fire Coordinator) | [9 empty] | 12%
| 16 | Service to critical facilities, water, communication, health, public protection (TDAM, CISCO) | [9 empty] | 3%
| 17 | Ranking by environmental | [9 empty] | 3%
| 18 | Ranking by cultural | [9 empty] | 3% | 21%
[11 empty] | TOTAL |  | 96%
Italic = open switch (tie or fuse bypass)

## excess_outage
Speed | Km/h | LogRelative5 | Err Low | Err High |  | Fit
5 | 8.05 | 0 | 0.055708 | 0.049368 | 0 | 0
10 | 16.1 | 0.23957 | 0.055708 | 0.049368 | 5 | 0.3163
15 | 24.15 | 0.619 | 0.056143 | 0.049709 | 10 | 0.6326
20 | 32.2 | 1.0545 | 0.049862 | 0.044722 | 15 | 0.94891
25 | 40.25 | 1.1258 | 0.037517 | 0.034532 | 20 | 1.2652
30 | 48.3 | 1.4467 | 0.050175 | 0.044974 | 25 | 1.5815
35 | 56.35 | 1.3822 | 0.048662 | 0.043755 | 30 | 1.8978
40 | 64.4 | 1.7642 | 0.041214 | 0.03764 | 35 | 2.2141
45 | 72.45 | 2.1991 | 0.047817 | 0.04307 | 40 | 2.5304
50 | 80.5 | 2.5392 | 0.055708 | 0.049368 | 45 | 2.8467
55 | 88.55 | 3.3556 | 0.076871 | 0.065289 | 50 | 3.163
60 | 96.6 | 4.2722 | 0.09097 | 0.075175 | 55 | 3.4793
65 | 104.65 | 3.965 | 0.30103 | 0.17609 | 60 | 3.7956
70 | 112.7 | 4.1269 | 4.1269 | 0.30103
75 | 120.75
80 | 128.8
|  |  | 0.06326 | 0
|  |  | 0.0027004 | #N/A
|  |  | 0.9786 | 0.34423
|  |  | 548.7966 | 12
|  |  | 65.0307 | 1.422